## Index
INDEX | Technology Data for Industrial Process Heat
1.1 Traditional heat pump | All cost data is in 2025€
1.2 heat_cool hp 80 C 75 K
2.a High temp. hp Up to 125C
2.b High temp. hp Up to 150
4 MVR 5 K
5.1a Electric boiler steam | Date | Sheet | Change | Notes
5.1b Electric boiler steam | 2026-01-05 | All | Update and simplification of datasheets on heat pumps, high temperature heat pumps, boilers and direct eletric firing. Adjusted all prices to be 2025 Euro, instead of 2019. New formatting and creation of the all data flat sheet.
5.2a Electric boiler hot wate
5.2b Electric boiler hot wate
6.1 Boiler, gas and oil | 2022-12-15 | 310.1a-310.2b | Electric boilers replaced and updated
6.2 Boiler, biomass | 2021-11-01 | 401-403 CC | Carbon capture removed and transferred to the Technology Catalogue for Carbon Capture, Transport and Storage
6.3 Boiler, coal | 2020-10-01 | 401-403 CC | Carbon capture added
7.1 Direct firing Natural Gas
7.2 Direct firing Solid Fuels
7.3 Direct electric firing
This file contains the technology data sheets related to industrial process heat. The data sheets are continuously updated as technologies evolve, if the data changes significantly or if errors are found. Dates and descriptions of updates are listed in the ammendment sheet below.

## alldata_flat
ws | Technology | cat | par | unit | priceyear | note | ref | est | year | val
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 2 | ctrl | 2025 | 0.01
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 2 | ctrl | 2030 | 0.01
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 2 | ctrl | 2035 | 0.01
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 2 | ctrl | 2040 | 0.01
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 2 | ctrl | 2050 | 0.01
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 2 | lower | 2025 | 0.01
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 2 | lower | 2050 | 0.01
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 2 | upper | 2025 | 0.04
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 2 | upper | 2050 | 0.04
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Construction time [years] | years |  |  | 2 | ctrl | 2025 | 0.5
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Construction time [years] | years |  |  | 2 | ctrl | 2030 | 0.5
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Construction time [years] | years |  |  | 2 | ctrl | 2035 | 0.5
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Construction time [years] | years |  |  | 2 | ctrl | 2040 | 0.5
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Construction time [years] | years |  |  | 2 | ctrl | 2050 | 0.5
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Construction time [years] | years |  |  | 2 | lower | 2025 | 0.3
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Construction time [years] | years |  |  | 2 | lower | 2050 | 0.3
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Construction time [years] | years |  |  | 2 | upper | 2025 | 1
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Construction time [years] | years |  |  | 2 | upper | 2050 | 1
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Forced outage [%] | pct. |  | D | 2 | ctrl | 2025 | 0
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Forced outage [%] | pct. |  | D | 2 | ctrl | 2030 | 0
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Forced outage [%] | pct. |  | D | 2 | ctrl | 2035 | 0
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Forced outage [%] | pct. |  | D | 2 | ctrl | 2040 | 0
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Forced outage [%] | pct. |  | D | 2 | ctrl | 2050 | 0
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Forced outage [%] | pct. |  | D | 2 | lower | 2025 | 0
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Forced outage [%] | pct. |  | D | 2 | lower | 2050 | 0
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Forced outage [%] | pct. |  | D | 2 | upper | 2025 | 0.01
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Forced outage [%] | pct. |  | D | 2 | upper | 2050 | 0.01
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A | [1, 2] | ctrl | 2025 | 3
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A | [1, 2] | ctrl | 2030 | 3
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A | [1, 2] | ctrl | 2035 | 3
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A | [1, 2] | ctrl | 2040 | 3
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A | [1, 2] | ctrl | 2050 | 3
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A | [1, 2] | lower | 2025 | 0.5
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A | [1, 2] | lower | 2050 | 0.5
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A | [1, 2] | upper | 2025 | 5
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A | [1, 2] | upper | 2050 | 5
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | ctrl | 2025 | 1
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | ctrl | 2030 | 1
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | ctrl | 2035 | 1
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | ctrl | 2040 | 1
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | ctrl | 2050 | 1
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | lower | 2025 | 0.5
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | lower | 2050 | 0.5
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | upper | 2025 | 2
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | upper | 2050 | 2
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | ctrl | 2025 | 25
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | ctrl | 2030 | 25
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | ctrl | 2035 | 25
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | ctrl | 2040 | 25
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | ctrl | 2050 | 25
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | lower | 2025 | 15
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | lower | 2050 | 15
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | upper | 2025 | 40
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | upper | 2050 | 40
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | B,C |  | ctrl | 2025 | 5.28
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | B,C |  | ctrl | 2030 | 5.4399
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | B,C |  | ctrl | 2035 | 5.5
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | B,C |  | ctrl | 2040 | 5.5497
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | B,C |  | ctrl | 2050 | 5.6057
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | B,C |  | lower | 2025 | 5.28
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | B,C |  | lower | 2050 | 5.436
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | B,C |  | upper | 2025 | 5.5465
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | B,C |  | upper | 2050 | 5.7188
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | B | [1, 3] | ctrl | 2025 | 5.33
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | B | [1, 3] | ctrl | 2030 | 5.4899
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | B | [1, 3] | ctrl | 2035 | 5.55
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | B | [1, 3] | ctrl | 2040 | 5.5997
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | B | [1, 3] | ctrl | 2050 | 5.6557
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | B | [1, 3] | lower | 2025 | 5.33
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | B | [1, 3] | lower | 2050 | 5.486
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | B | [1, 3] | upper | 2025 | 5.5965
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | B | [1, 3] | upper | 2050 | 5.7688
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | - of which equipment [%] | pct. |  | E | 2 | ctrl | 2025 | 0.4
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | - of which equipment [%] | pct. |  | E | 2 | ctrl | 2030 | 0.4
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | - of which equipment [%] | pct. |  | E | 2 | ctrl | 2035 | 0.4
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | - of which equipment [%] | pct. |  | E | 2 | ctrl | 2040 | 0.4
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | - of which equipment [%] | pct. |  | E | 2 | ctrl | 2050 | 0.4
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | - of which installation and other costs [%] | pct. |  | F | 2 | ctrl | 2025 | 0.6
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | - of which installation and other costs [%] | pct. |  | F | 2 | ctrl | 2030 | 0.6
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | - of which installation and other costs [%] | pct. |  | F | 2 | ctrl | 2035 | 0.6
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | - of which installation and other costs [%] | pct. |  | F | 2 | ctrl | 2040 | 0.6
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | - of which installation and other costs [%] | pct. |  | F | 2 | ctrl | 2050 | 0.6
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | 2 | ctrl | 2025 | 2127
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | 2 | ctrl | 2030 | 2095
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | 2 | ctrl | 2035 | 2032
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | 2 | ctrl | 2040 | 2032
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | 2 | ctrl | 2050 | 2001
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | 2 | lower | 2025 | 2032
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | 2 | lower | 2050 | 1970
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | 2 | upper | 2025 | 2127
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | 2 | upper | 2050 | 2127
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | Nominal investment [M€/MW] | M€/MW |  |  | 2 | ctrl | 2025 | 0.95
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | Nominal investment [M€/MW] | M€/MW |  |  | 2 | ctrl | 2030 | 0.94
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | Nominal investment [M€/MW] | M€/MW |  |  | 2 | ctrl | 2035 | 0.91
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | Nominal investment [M€/MW] | M€/MW |  |  | 2 | ctrl | 2040 | 0.91
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | Nominal investment [M€/MW] | M€/MW |  |  | 2 | ctrl | 2050 | 0.89
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | Nominal investment [M€/MW] | M€/MW |  |  | 2 | lower | 2025 | 0.91
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | Nominal investment [M€/MW] | M€/MW |  |  | 2 | lower | 2050 | 0.88
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | Nominal investment [M€/MW] | M€/MW |  |  | 2 | upper | 2025 | 0.95
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | Nominal investment [M€/MW] | M€/MW |  |  | 2 | upper | 2050 | 0.95
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | 2 | ctrl | 2025 | 3.07
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | 2 | ctrl | 2030 | 3.02
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | 2 | ctrl | 2035 | 2.93
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | 2 | ctrl | 2040 | 2.93
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | 2 | ctrl | 2050 | 2.89
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | 2 | lower | 2025 | 2.93
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | 2 | lower | 2050 | 2.84
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | 2 | upper | 2025 | 3.07
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | 2 | upper | 2050 | 3.07
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Regulation Ability | Cold start-up time [hours] | hours |  |  | 2 | ctrl | 2025 | 1
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Regulation Ability | Cold start-up time [hours] | hours |  |  | 2 | ctrl | 2030 | 1
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Regulation Ability | Cold start-up time [hours] | hours |  |  | 2 | ctrl | 2035 | 1
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Regulation Ability | Cold start-up time [hours] | hours |  |  | 2 | ctrl | 2040 | 1
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Regulation Ability | Cold start-up time [hours] | hours |  |  | 2 | ctrl | 2050 | 1
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Regulation Ability | Cold start-up time [hours] | hours |  |  | 2 | lower | 2025 | 0.2
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Regulation Ability | Cold start-up time [hours] | hours |  |  | 2 | lower | 2050 | 0.2
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Regulation Ability | Cold start-up time [hours] | hours |  |  | 2 | upper | 2025 | 1
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Regulation Ability | Cold start-up time [hours] | hours |  |  | 2 | upper | 2050 | 1
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 2 | ctrl | 2025 | 0.25
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 2 | ctrl | 2030 | 0.25
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 2 | ctrl | 2035 | 0.25
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 2 | ctrl | 2040 | 0.25
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 2 | ctrl | 2050 | 0.25
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 2 | lower | 2025 | 0.1
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 2 | lower | 2050 | 0.1
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 2 | upper | 2025 | 0.5
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 2 | upper | 2050 | 0.5
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Regulation Ability | Warm start-up time [hours] | hours |  |  | 2 | ctrl | 2025 | 0.1
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Regulation Ability | Warm start-up time [hours] | hours |  |  | 2 | ctrl | 2030 | 0.1
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Regulation Ability | Warm start-up time [hours] | hours |  |  | 2 | ctrl | 2035 | 0.1
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Regulation Ability | Warm start-up time [hours] | hours |  |  | 2 | ctrl | 2040 | 0.1
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Regulation Ability | Warm start-up time [hours] | hours |  |  | 2 | ctrl | 2050 | 0.1
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Regulation Ability | Warm start-up time [hours] | hours |  |  | 2 | lower | 2025 | 0.1
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Regulation Ability | Warm start-up time [hours] | hours |  |  | 2 | lower | 2050 | 0.1
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Regulation Ability | Warm start-up time [hours] | hours |  |  | 2 | upper | 2025 | 0.2
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Regulation Ability | Warm start-up time [hours] | hours |  |  | 2 | upper | 2050 | 0.2
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 50 K, 70°C max | pct. |  | G |  | ctrl | 2025 | 4.52
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 50 K, 70°C max | pct. |  | G |  | ctrl | 2030 | 4.6
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 50 K, 70°C max | pct. |  | G |  | ctrl | 2035 | 4.65
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 50 K, 70°C max | pct. |  | G |  | ctrl | 2040 | 4.7
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 50 K, 70°C max | pct. |  | G |  | ctrl | 2050 | 4.74
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 50 K, 70°C max | pct. |  | G |  | lower | 2025 | 4.47
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 50 K, 70°C max | pct. |  | G |  | lower | 2050 | 4.6
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 50 K, 70°C max | pct. |  | G |  | upper | 2025 | 4.69
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 50 K, 70°C max | pct. |  | G |  | upper | 2050 | 4.84
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 60 K, 80°C max | pct. |  | G |  | ctrl | 2025 | 3.95
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 60 K, 80°C max | pct. |  | G |  | ctrl | 2030 | 4
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 60 K, 80°C max | pct. |  | G |  | ctrl | 2035 | 4.04
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 60 K, 80°C max | pct. |  | G |  | ctrl | 2040 | 4.08
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 60 K, 80°C max | pct. |  | G |  | ctrl | 2050 | 4.12
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 60 K, 80°C max | pct. |  | G |  | lower | 2025 | 3.88
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 60 K, 80°C max | pct. |  | G |  | lower | 2050 | 3.99
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 60 K, 80°C max | pct. |  | G |  | upper | 2025 | 4.07
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 60 K, 80°C max | pct. |  | G |  | upper | 2050 | 4.2
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | Cooling generation capacity for one unit [MW] | MW |  |  |  | ctrl | 2025 | -
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | Cooling generation capacity for one unit [MW] | MW |  |  |  | ctrl | 2030 | -
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | Cooling generation capacity for one unit [MW] | MW |  |  |  | ctrl | 2035 | -
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | Cooling generation capacity for one unit [MW] | MW |  |  |  | ctrl | 2040 | -
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | Cooling generation capacity for one unit [MW] | MW |  |  |  | ctrl | 2050 | -
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | Indirect investments cost [M€/MW] | M€/MW |  | H |  | ctrl | 2025 | 0.19
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | Indirect investments cost [M€/MW] | M€/MW |  | H |  | ctrl | 2030 | 0.188
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | Indirect investments cost [M€/MW] | M€/MW |  | H |  | ctrl | 2035 | 0.182
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | Indirect investments cost [M€/MW] | M€/MW |  | H |  | ctrl | 2040 | 0.182
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | Indirect investments cost [M€/MW] | M€/MW |  | H |  | ctrl | 2050 | 0.178
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | Non energy gains [M€/MW] | M€/MW |  |  |  | ctrl | 2025 | -
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | Non energy gains [M€/MW] | M€/MW |  |  |  | ctrl | 2030 | -
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | Non energy gains [M€/MW] | M€/MW |  |  |  | ctrl | 2035 | -
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | Non energy gains [M€/MW] | M€/MW |  |  |  | ctrl | 2040 | -
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | Non energy gains [M€/MW] | M€/MW |  |  |  | ctrl | 2050 | -
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | Startup cost [€/MW/startup] | €/MW/startup |  |  |  | ctrl | 2025 | 10
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | Startup cost [€/MW/startup] | €/MW/startup |  |  |  | ctrl | 2030 | 10
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | Startup cost [€/MW/startup] | €/MW/startup |  |  |  | ctrl | 2035 | 10
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | Startup cost [€/MW/startup] | €/MW/startup |  |  |  | ctrl | 2040 | 10
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | Startup cost [€/MW/startup] | €/MW/startup |  |  |  | ctrl | 2050 | 10
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | Temperature heat source return [°C] | °C |  | I |  | ctrl | 2025 | 20
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | Temperature heat source return [°C] | °C |  | I |  | ctrl | 2030 | 20
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | Temperature heat source return [°C] | °C |  | I |  | ctrl | 2035 | 20
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | Temperature heat source return [°C] | °C |  | I |  | ctrl | 2040 | 20
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | Temperature heat source return [°C] | °C |  | I |  | ctrl | 2050 | 20
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | Temperature heat source supply [°C] | °C |  | I |  | ctrl | 2025 | 30
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | Temperature heat source supply [°C] | °C |  | I |  | ctrl | 2030 | 30
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | Temperature heat source supply [°C] | °C |  | I |  | ctrl | 2035 | 30
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | Temperature heat source supply [°C] | °C |  | I |  | ctrl | 2040 | 30
1.1 Traditional heat pump | Heat pump, up to 60 °C, Temp lift = 40 K | Technology-specific data | Temperature heat source supply [°C] | °C |  | I |  | ctrl | 2050 | 30
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 2 | ctrl | 2025 | 0.01
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 2 | ctrl | 2030 | 0.01
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 2 | ctrl | 2035 | 0.01
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 2 | ctrl | 2040 | 0.01
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 2 | ctrl | 2050 | 0.01
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 2 | lower | 2025 | 0.01
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 2 | lower | 2050 | 0.01
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 2 | upper | 2025 | 0.04
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 2 | upper | 2050 | 0.04
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Construction time [years] | years |  |  | 2 | ctrl | 2025 | 0.5
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Construction time [years] | years |  |  | 2 | ctrl | 2030 | 0.5
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Construction time [years] | years |  |  | 2 | ctrl | 2035 | 0.5
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Construction time [years] | years |  |  | 2 | ctrl | 2040 | 0.5
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Construction time [years] | years |  |  | 2 | ctrl | 2050 | 0.5
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Construction time [years] | years |  |  | 2 | lower | 2025 | 0.3
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Construction time [years] | years |  |  | 2 | lower | 2050 | 0.3
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Construction time [years] | years |  |  | 2 | upper | 2025 | 1
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Construction time [years] | years |  |  | 2 | upper | 2050 | 1
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Forced outage [%] | pct. |  | D | 2 | ctrl | 2025 | 0
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Forced outage [%] | pct. |  | D | 2 | ctrl | 2030 | 0
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Forced outage [%] | pct. |  | D | 2 | ctrl | 2035 | 0
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Forced outage [%] | pct. |  | D | 2 | ctrl | 2040 | 0
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Forced outage [%] | pct. |  | D | 2 | ctrl | 2050 | 0
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Forced outage [%] | pct. |  | D | 2 | lower | 2025 | 0
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Forced outage [%] | pct. |  | D | 2 | lower | 2050 | 0
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Forced outage [%] | pct. |  | D | 2 | upper | 2025 | 0.01
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Forced outage [%] | pct. |  | D | 2 | upper | 2050 | 0.01
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A | [1, 2] | ctrl | 2025 | 3
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A | [1, 2] | ctrl | 2030 | 3
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A | [1, 2] | ctrl | 2035 | 3
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A | [1, 2] | ctrl | 2040 | 3
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A | [1, 2] | ctrl | 2050 | 3
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A | [1, 2] | lower | 2025 | 0.5
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A | [1, 2] | lower | 2050 | 0.5
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A | [1, 2] | upper | 2025 | 5
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A | [1, 2] | upper | 2050 | 5
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | ctrl | 2025 | 1
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | ctrl | 2030 | 1
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | ctrl | 2035 | 1
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | ctrl | 2040 | 1
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | ctrl | 2050 | 1
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | lower | 2025 | 0.5
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | lower | 2050 | 0.5
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | upper | 2025 | 2
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | upper | 2050 | 2
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | ctrl | 2025 | 25
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | ctrl | 2030 | 25
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | ctrl | 2035 | 25
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | ctrl | 2040 | 25
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | ctrl | 2050 | 25
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | lower | 2025 | 15
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | lower | 2050 | 15
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | upper | 2025 | 40
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | upper | 2050 | 40
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | B,C |  | ctrl | 2025 | 3.3
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | B,C |  | ctrl | 2030 | 3.38
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | B,C |  | ctrl | 2035 | 3.43
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | B,C |  | ctrl | 2040 | 3.4486
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | B,C |  | ctrl | 2050 | 3.4836
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | B,C |  | lower | 2025 | 3.28
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | B,C |  | lower | 2050 | 3.3776
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | B,C |  | upper | 2025 | 3.4675
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | B,C |  | upper | 2050 | 3.5543
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | B | [1, 3] | ctrl | 2025 | 3.35
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | B | [1, 3] | ctrl | 2030 | 3.43
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | B | [1, 3] | ctrl | 2035 | 3.48
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | B | [1, 3] | ctrl | 2040 | 3.4986
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | B | [1, 3] | ctrl | 2050 | 3.5336
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | B | [1, 3] | lower | 2025 | 3.33
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | B | [1, 3] | lower | 2050 | 3.4276
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | B | [1, 3] | upper | 2025 | 3.5175
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | B | [1, 3] | upper | 2050 | 3.6043
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | - of which equipment [%] | pct. |  | E | 2 | ctrl | 2025 | 0.4
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | - of which equipment [%] | pct. |  | E | 2 | ctrl | 2030 | 0.4
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | - of which equipment [%] | pct. |  | E | 2 | ctrl | 2035 | 0.4
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | - of which equipment [%] | pct. |  | E | 2 | ctrl | 2040 | 0.4
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | - of which equipment [%] | pct. |  | E | 2 | ctrl | 2050 | 0.4
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | - of which installation and other costs [%] | pct. |  | F | 2 | ctrl | 2025 | 0.6
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | - of which installation and other costs [%] | pct. |  | F | 2 | ctrl | 2030 | 0.6
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | - of which installation and other costs [%] | pct. |  | F | 2 | ctrl | 2035 | 0.6
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | - of which installation and other costs [%] | pct. |  | F | 2 | ctrl | 2040 | 0.6
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | - of which installation and other costs [%] | pct. |  | F | 2 | ctrl | 2050 | 0.6
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | 2 | ctrl | 2025 | 2127
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | 2 | ctrl | 2030 | 2095
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | 2 | ctrl | 2035 | 2032
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | 2 | ctrl | 2040 | 2032
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | 2 | ctrl | 2050 | 2001
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | 2 | lower | 2025 | 2032
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | 2 | lower | 2050 | 1970
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | 2 | upper | 2025 | 2127
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | 2 | upper | 2050 | 2127
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | Nominal investment [M€/MW] | M€/MW |  |  | 2 | ctrl | 2025 | 0.95
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | Nominal investment [M€/MW] | M€/MW |  |  | 2 | ctrl | 2030 | 0.94
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | Nominal investment [M€/MW] | M€/MW |  |  | 2 | ctrl | 2035 | 0.91
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | Nominal investment [M€/MW] | M€/MW |  |  | 2 | ctrl | 2040 | 0.91
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | Nominal investment [M€/MW] | M€/MW |  |  | 2 | ctrl | 2050 | 0.89
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | Nominal investment [M€/MW] | M€/MW |  |  | 2 | lower | 2025 | 0.91
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | Nominal investment [M€/MW] | M€/MW |  |  | 2 | lower | 2050 | 0.88
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | Nominal investment [M€/MW] | M€/MW |  |  | 2 | upper | 2025 | 0.95
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | Nominal investment [M€/MW] | M€/MW |  |  | 2 | upper | 2050 | 0.95
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | 2 | ctrl | 2025 | 3.07
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | 2 | ctrl | 2030 | 3.02
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | 2 | ctrl | 2035 | 2.93
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | 2 | ctrl | 2040 | 2.93
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | 2 | ctrl | 2050 | 2.89
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | 2 | lower | 2025 | 2.93
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | 2 | lower | 2050 | 2.84
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | 2 | upper | 2025 | 3.07
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | 2 | upper | 2050 | 3.07
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Regulation Ability | Cold start-up time [hours] | hours |  |  | 2 | ctrl | 2025 | 1
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Regulation Ability | Cold start-up time [hours] | hours |  |  | 2 | ctrl | 2030 | 1
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Regulation Ability | Cold start-up time [hours] | hours |  |  | 2 | ctrl | 2035 | 1
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Regulation Ability | Cold start-up time [hours] | hours |  |  | 2 | ctrl | 2040 | 1
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Regulation Ability | Cold start-up time [hours] | hours |  |  | 2 | ctrl | 2050 | 1
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Regulation Ability | Cold start-up time [hours] | hours |  |  | 2 | lower | 2025 | 0.2
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Regulation Ability | Cold start-up time [hours] | hours |  |  | 2 | lower | 2050 | 0.2
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Regulation Ability | Cold start-up time [hours] | hours |  |  | 2 | upper | 2025 | 1
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Regulation Ability | Cold start-up time [hours] | hours |  |  | 2 | upper | 2050 | 1
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 2 | ctrl | 2025 | 0.25
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 2 | ctrl | 2030 | 0.25
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 2 | ctrl | 2035 | 0.25
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 2 | ctrl | 2040 | 0.25
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 2 | ctrl | 2050 | 0.25
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 2 | lower | 2025 | 0.1
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 2 | lower | 2050 | 0.1
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 2 | upper | 2025 | 0.5
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 2 | upper | 2050 | 0.5
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Regulation Ability | Warm start-up time [hours] | hours |  |  | 2 | ctrl | 2025 | 0.1
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Regulation Ability | Warm start-up time [hours] | hours |  |  | 2 | ctrl | 2030 | 0.1
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Regulation Ability | Warm start-up time [hours] | hours |  |  | 2 | ctrl | 2035 | 0.1
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Regulation Ability | Warm start-up time [hours] | hours |  |  | 2 | ctrl | 2040 | 0.1
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Regulation Ability | Warm start-up time [hours] | hours |  |  | 2 | ctrl | 2050 | 0.1
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Regulation Ability | Warm start-up time [hours] | hours |  |  | 2 | lower | 2025 | 0.1
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Regulation Ability | Warm start-up time [hours] | hours |  |  | 2 | lower | 2050 | 0.1
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Regulation Ability | Warm start-up time [hours] | hours |  |  | 2 | upper | 2025 | 0.2
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Regulation Ability | Warm start-up time [hours] | hours |  |  | 2 | upper | 2050 | 0.2
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Technology-specific data | Cooling generation capacity for one unit [MW] | MW |  |  |  | ctrl | 2025 | -86.5522
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Technology-specific data | Cooling generation capacity for one unit [MW] | MW |  |  |  | ctrl | 2030 | -84.4636
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Technology-specific data | Cooling generation capacity for one unit [MW] | MW |  |  |  | ctrl | 2035 | -83.2069
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Technology-specific data | Cooling generation capacity for one unit [MW] | MW |  |  |  | ctrl | 2040 | -82.7486
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Technology-specific data | Cooling generation capacity for one unit [MW] | MW |  |  |  | ctrl | 2050 | -81.8996
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Technology-specific data | Indirect investments cost [M€/MW] | M€/MW |  | H |  | ctrl | 2025 | 0.19
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Technology-specific data | Indirect investments cost [M€/MW] | M€/MW |  | H |  | ctrl | 2030 | 0.188
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Technology-specific data | Indirect investments cost [M€/MW] | M€/MW |  | H |  | ctrl | 2035 | 0.182
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Technology-specific data | Indirect investments cost [M€/MW] | M€/MW |  | H |  | ctrl | 2040 | 0.182
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Technology-specific data | Indirect investments cost [M€/MW] | M€/MW |  | H |  | ctrl | 2050 | 0.178
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Technology-specific data | Non energy gains [M€/MW] | M€/MW |  |  |  | ctrl | 2025 | -
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Technology-specific data | Non energy gains [M€/MW] | M€/MW |  |  |  | ctrl | 2030 | -
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Technology-specific data | Non energy gains [M€/MW] | M€/MW |  |  |  | ctrl | 2035 | -
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Technology-specific data | Non energy gains [M€/MW] | M€/MW |  |  |  | ctrl | 2040 | -
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Technology-specific data | Non energy gains [M€/MW] | M€/MW |  |  |  | ctrl | 2050 | -
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Technology-specific data | Startup cost [€/MW/startup] | €/MW/startup |  |  |  | ctrl | 2025 | 10
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Technology-specific data | Startup cost [€/MW/startup] | €/MW/startup |  |  |  | ctrl | 2030 | 10
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Technology-specific data | Startup cost [€/MW/startup] | €/MW/startup |  |  |  | ctrl | 2035 | 10
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Technology-specific data | Startup cost [€/MW/startup] | €/MW/startup |  |  |  | ctrl | 2040 | 10
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Technology-specific data | Startup cost [€/MW/startup] | €/MW/startup |  |  |  | ctrl | 2050 | 10
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Technology-specific data | Temperature heat source return [°C] | °C |  | I |  | ctrl | 2025 | 5
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Technology-specific data | Temperature heat source return [°C] | °C |  | I |  | ctrl | 2030 | 5
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Technology-specific data | Temperature heat source return [°C] | °C |  | I |  | ctrl | 2035 | 5
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Technology-specific data | Temperature heat source return [°C] | °C |  | I |  | ctrl | 2040 | 5
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Technology-specific data | Temperature heat source return [°C] | °C |  | I |  | ctrl | 2050 | 5
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Technology-specific data | Temperature heat source supply [°C] | °C |  | I |  | ctrl | 2025 | 15
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Technology-specific data | Temperature heat source supply [°C] | °C |  | I |  | ctrl | 2030 | 15
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Technology-specific data | Temperature heat source supply [°C] | °C |  | I |  | ctrl | 2035 | 15
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Technology-specific data | Temperature heat source supply [°C] | °C |  | I |  | ctrl | 2040 | 15
1.2 heat_cool hp 80 C 75 K | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K | Technology-specific data | Temperature heat source supply [°C] | °C |  | I |  | ctrl | 2050 | 15
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 1 | ctrl | 2025 | 0.02
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 1 | ctrl | 2030 | 0.02
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 1 | ctrl | 2035 | 0.02
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 1 | ctrl | 2040 | 0.02
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 1 | ctrl | 2050 | 0.02
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 1 | lower | 2025 | 0.01
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 1 | lower | 2050 | 0.01
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 1 | upper | 2025 | 0.07
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 1 | upper | 2050 | 0.07
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Construction time [years] | years |  | E | 4 | ctrl | 2025 | 0.6
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Construction time [years] | years |  | E | 4 | ctrl | 2030 | 0.5
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Construction time [years] | years |  | E | 4 | ctrl | 2035 | 0.4
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Construction time [years] | years |  | E | 4 | ctrl | 2040 | 0.4
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Construction time [years] | years |  | E | 4 | ctrl | 2050 | 0.4
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Construction time [years] | years |  | E | 4 | lower | 2025 | 0.4
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Construction time [years] | years |  | E | 4 | lower | 2050 | 0.2
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Construction time [years] | years |  | E | 4 | upper | 2025 | 0.8
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Construction time [years] | years |  | E | 4 | upper | 2050 | 0.8
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Forced outage [days] | days |  |  | 4 | ctrl | 2025 | 0
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Forced outage [days] | days |  |  | 4 | ctrl | 2030 | 0
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Forced outage [days] | days |  |  | 4 | ctrl | 2035 | 0
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Forced outage [days] | days |  |  | 4 | ctrl | 2040 | 0
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Forced outage [days] | days |  |  | 4 | ctrl | 2050 | 0
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Forced outage [days] | days |  |  | 4 | lower | 2025 | 0
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Forced outage [days] | days |  |  | 4 | lower | 2050 | 0
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Forced outage [days] | days |  |  | 4 | upper | 2025 | 1
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Forced outage [days] | days |  |  | 4 | upper | 2050 | 1
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | B | 4 | ctrl | 2025 | 2
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | B | 4 | ctrl | 2030 | 2
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | B | 4 | ctrl | 2035 | 3
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | B | 4 | ctrl | 2040 | 3
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | B | 4 | ctrl | 2050 | 3
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | B | 4 | lower | 2025 | 0.3
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | B | 4 | lower | 2050 | 0.2
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | B | 4 | upper | 2025 | 25
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | B | 4 | upper | 2050 | 50
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 4 | ctrl | 2025 | 0.5
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 4 | ctrl | 2030 | 0.5
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 4 | ctrl | 2035 | 0.5
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 4 | ctrl | 2040 | 0.5
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 4 | ctrl | 2050 | 0.5
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 4 | lower | 2025 | 0
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 4 | lower | 2050 | 0
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 4 | upper | 2025 | 1
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 4 | upper | 2050 | 1
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2025 | 0.02
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2030 | 0.02
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2035 | 0.02
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2040 | 0.02
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2050 | 0.02
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2025 | 0.01
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2050 | 0.01
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2025 | 0.04
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2050 | 0.04
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Technical lifetime [years] | years |  | D | 4 | ctrl | 2025 | 20
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Technical lifetime [years] | years |  | D | 4 | ctrl | 2030 | 20
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Technical lifetime [years] | years |  | D | 4 | ctrl | 2035 | 20
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Technical lifetime [years] | years |  | D | 4 | ctrl | 2040 | 20
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Technical lifetime [years] | years |  | D | 4 | ctrl | 2050 | 20
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Technical lifetime [years] | years |  | D | 4 | lower | 2025 | 15
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Technical lifetime [years] | years |  | D | 4 | lower | 2050 | 15
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Technical lifetime [years] | years |  | D | 4 | upper | 2025 | 30
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Technical lifetime [years] | years |  | D | 4 | upper | 2050 | 30
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  |  | ctrl | 2025 | 2.7
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  |  | ctrl | 2030 | 2.8
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  |  | ctrl | 2035 | 2.85
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  |  | ctrl | 2040 | 2.9
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  |  | ctrl | 2050 | 2.95
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  |  | lower | 2025 | 2.2
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  |  | lower | 2050 | 2.45
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  |  | upper | 2025 | 3.95
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  |  | upper | 2050 | 4.45
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Total efficiency, net [%], nominel load. Based on a temperature lift of 65 K | pct. |  | C, H | 1 | ctrl | 2025 | 2.75
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Total efficiency, net [%], nominel load. Based on a temperature lift of 65 K | pct. |  | C, H | 1 | ctrl | 2030 | 2.85
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Total efficiency, net [%], nominel load. Based on a temperature lift of 65 K | pct. |  | C, H | 1 | ctrl | 2035 | 2.9
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Total efficiency, net [%], nominel load. Based on a temperature lift of 65 K | pct. |  | C, H | 1 | ctrl | 2040 | 2.95
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Total efficiency, net [%], nominel load. Based on a temperature lift of 65 K | pct. |  | C, H | 1 | ctrl | 2050 | 3
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Total efficiency, net [%], nominel load. Based on a temperature lift of 65 K | pct. |  | C, H | 1 | lower | 2025 | 2.25
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Total efficiency, net [%], nominel load. Based on a temperature lift of 65 K | pct. |  | C, H | 1 | lower | 2050 | 2.5
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Total efficiency, net [%], nominel load. Based on a temperature lift of 65 K | pct. |  | C, H | 1 | upper | 2025 | 4
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Energy/technical data | Total efficiency, net [%], nominel load. Based on a temperature lift of 65 K | pct. |  | C, H | 1 | upper | 2050 | 4.5
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | - of which equipment [%] | pct. |  | A | 1 | ctrl | 2025 | 0.4
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | - of which equipment [%] | pct. |  | A | 1 | ctrl | 2030 | 0.4
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | - of which equipment [%] | pct. |  | A | 1 | ctrl | 2035 | 0.4
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | - of which equipment [%] | pct. |  | A | 1 | ctrl | 2040 | 0.4
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | - of which equipment [%] | pct. |  | A | 1 | ctrl | 2050 | 0.4
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | - of which equipment [%] | pct. |  | A | 1 | lower | 2025 | 0.25
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | - of which equipment [%] | pct. |  | A | 1 | lower | 2050 | 0.25
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | - of which equipment [%] | pct. |  | A | 1 | upper | 2025 | 0.6
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | - of which equipment [%] | pct. |  | A | 1 | upper | 2050 | 0.7
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | - of which installation [%] | pct. |  | A | 3 | ctrl | 2025 | 0.6
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | - of which installation [%] | pct. |  | A | 3 | ctrl | 2030 | 0.6
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | - of which installation [%] | pct. |  | A | 3 | ctrl | 2035 | 0.6
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | - of which installation [%] | pct. |  | A | 3 | ctrl | 2040 | 0.6
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | - of which installation [%] | pct. |  | A | 3 | ctrl | 2050 | 0.6
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | - of which installation [%] | pct. |  | A | 3 | lower | 2025 | 0.4
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | - of which installation [%] | pct. |  | A | 3 | lower | 2050 | 0.3
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | - of which installation [%] | pct. |  | A | 3 | upper | 2025 | 0.75
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | - of which installation [%] | pct. |  | A | 3 | upper | 2050 | 0.75
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | Fixed O&M [EUR/MW_y] | EUR/MW_y | 2025 |  | 2 | ctrl | 2025 | 2494
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | Fixed O&M [EUR/MW_y] | EUR/MW_y | 2025 |  | 2 | ctrl | 2030 | 2456
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | Fixed O&M [EUR/MW_y] | EUR/MW_y | 2025 |  | 2 | ctrl | 2035 | 2382
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | Fixed O&M [EUR/MW_y] | EUR/MW_y | 2025 |  | 2 | ctrl | 2040 | 2382
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | Fixed O&M [EUR/MW_y] | EUR/MW_y | 2025 |  | 2 | ctrl | 2050 | 2345
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | Nominal investment (*total) [MEUR/MW] | MEUR/MW | 2025 | G | [1, 4] | ctrl | 2025 | 1.2
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | Nominal investment (*total) [MEUR/MW] | MEUR/MW | 2025 | G | [1, 4] | ctrl | 2030 | 1.15
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | Nominal investment (*total) [MEUR/MW] | MEUR/MW | 2025 | G | [1, 4] | ctrl | 2035 | 1.1
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | Nominal investment (*total) [MEUR/MW] | MEUR/MW | 2025 | G | [1, 4] | ctrl | 2040 | 1.05
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | Nominal investment (*total) [MEUR/MW] | MEUR/MW | 2025 | G | [1, 4] | ctrl | 2050 | 1
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | Nominal investment (*total) [MEUR/MW] | MEUR/MW | 2025 | G | [1, 4] | lower | 2025 | 0.9
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | Nominal investment (*total) [MEUR/MW] | MEUR/MW | 2025 | G | [1, 4] | lower | 2050 | 0.7
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | Nominal investment (*total) [MEUR/MW] | MEUR/MW | 2025 | G | [1, 4] | upper | 2025 | 1.5
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | Nominal investment (*total) [MEUR/MW] | MEUR/MW | 2025 | G | [1, 4] | upper | 2050 | 1.3
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | Variable O&M [EUR/MWh] | EUR/MWh | 2025 |  | 2 | ctrl | 2025 | 3.6
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | Variable O&M [EUR/MWh] | EUR/MWh | 2025 |  | 2 | ctrl | 2030 | 3.54
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | Variable O&M [EUR/MWh] | EUR/MWh | 2025 |  | 2 | ctrl | 2035 | 3.43
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | Variable O&M [EUR/MWh] | EUR/MWh | 2025 |  | 2 | ctrl | 2040 | 3.43
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Financial data | Variable O&M [EUR/MWh] | EUR/MWh | 2025 |  | 2 | ctrl | 2050 | 3.39
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Cold start-up time [hours] | hours |  |  | 4 | ctrl | 2025 | 1
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Cold start-up time [hours] | hours |  |  | 4 | ctrl | 2030 | 1
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Cold start-up time [hours] | hours |  |  | 4 | ctrl | 2035 | 1
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Cold start-up time [hours] | hours |  |  | 4 | ctrl | 2040 | 1
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Cold start-up time [hours] | hours |  |  | 4 | ctrl | 2050 | 1
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Cold start-up time [hours] | hours |  |  | 4 | lower | 2025 | 0.5
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Cold start-up time [hours] | hours |  |  | 4 | lower | 2050 | 0.5
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Cold start-up time [hours] | hours |  |  | 4 | upper | 2025 | 1.5
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Cold start-up time [hours] | hours |  |  | 4 | upper | 2050 | 1.5
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Minimum load (of full load) [] |  |  | F | 4 | ctrl | 2025 | 0.25
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Minimum load (of full load) [] |  |  | F | 4 | ctrl | 2030 | 0.25
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Minimum load (of full load) [] |  |  | F | 4 | ctrl | 2035 | 0.25
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Minimum load (of full load) [] |  |  | F | 4 | ctrl | 2040 | 0.25
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Minimum load (of full load) [] |  |  | F | 4 | ctrl | 2050 | 0.25
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Minimum load (of full load) [] |  |  | F | 4 | lower | 2025 | 0.1
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Minimum load (of full load) [] |  |  | F | 4 | lower | 2050 | 0.1
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Minimum load (of full load) [] |  |  | F | 4 | upper | 2025 | 0.5
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Minimum load (of full load) [] |  |  | F | 4 | upper | 2050 | 0.5
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2025 | 0.05
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2030 | 0.07
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2035 | 0.08
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2040 | 0.09
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2050 | 0.1
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2025 | 0.02
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2050 | 0.05
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2025 | 0.1
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2050 | 0.2
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | ctrl | 2025 | 0.1
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | ctrl | 2030 | 0.14
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | ctrl | 2035 | 0.16
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | ctrl | 2040 | 0.18
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | ctrl | 2050 | 0.2
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | lower | 2025 | 0.04
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | lower | 2050 | 0.1
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | upper | 2025 | 0.2
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | upper | 2050 | 0.4
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Warm start-up time [hours] | hours |  |  | 4 | ctrl | 2025 | 0.25
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Warm start-up time [hours] | hours |  |  | 4 | ctrl | 2030 | 0.25
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Warm start-up time [hours] | hours |  |  | 4 | ctrl | 2035 | 0.25
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Warm start-up time [hours] | hours |  |  | 4 | ctrl | 2040 | 0.25
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Warm start-up time [hours] | hours |  |  | 4 | ctrl | 2050 | 0.25
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Warm start-up time [hours] | hours |  |  | 4 | lower | 2025 | 0.1
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Warm start-up time [hours] | hours |  |  | 4 | lower | 2050 | 0.1
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Warm start-up time [hours] | hours |  |  | 4 | upper | 2025 | 0.5
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Regulation ability | Warm start-up time [hours] | hours |  |  | 4 | upper | 2050 | 0.25
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Additional equipment cost for temperature lift above 75 K [MEUR/MW] | MEUR/MW | 2025 |  | [1, 4] | ctrl | 2025 | 0.15
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Additional equipment cost for temperature lift above 75 K [MEUR/MW] | MEUR/MW | 2025 |  | [1, 4] | ctrl | 2030 | 0.15
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Additional equipment cost for temperature lift above 75 K [MEUR/MW] | MEUR/MW | 2025 |  | [1, 4] | ctrl | 2035 | 0.15
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Additional equipment cost for temperature lift above 75 K [MEUR/MW] | MEUR/MW | 2025 |  | [1, 4] | ctrl | 2040 | 0.15
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Additional equipment cost for temperature lift above 75 K [MEUR/MW] | MEUR/MW | 2025 |  | [1, 4] | ctrl | 2050 | 0.1
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Additional equipment cost for temperature lift above 75 K [MEUR/MW] | MEUR/MW | 2025 |  | [1, 4] | lower | 2025 | 0.05
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Additional equipment cost for temperature lift above 75 K [MEUR/MW] | MEUR/MW | 2025 |  | [1, 4] | lower | 2050 | 0.05
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Additional equipment cost for temperature lift above 75 K [MEUR/MW] | MEUR/MW | 2025 |  | [1, 4] | upper | 2025 | 0.25
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Additional equipment cost for temperature lift above 75 K [MEUR/MW] | MEUR/MW | 2025 |  | [1, 4] | upper | 2050 | 0.25
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Steam generation decreases COP [%-point] | pct.-point |  |  | [1, 4] | ctrl | 2025 | -0.15
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Steam generation decreases COP [%-point] | pct.-point |  |  | [1, 4] | ctrl | 2030 | -0.1
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Steam generation decreases COP [%-point] | pct.-point |  |  | [1, 4] | ctrl | 2035 | -0.05
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Steam generation decreases COP [%-point] | pct.-point |  |  | [1, 4] | ctrl | 2040 | -0.05
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Steam generation decreases COP [%-point] | pct.-point |  |  | [1, 4] | ctrl | 2050 | -0.05
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Steam generation decreases COP [%-point] | pct.-point |  |  | [1, 4] | lower | 2025 | -0.05
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Steam generation decreases COP [%-point] | pct.-point |  |  | [1, 4] | lower | 2050 | -0.05
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Steam generation decreases COP [%-point] | pct.-point |  |  | [1, 4] | upper | 2025 | -0.2
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Steam generation decreases COP [%-point] | pct.-point |  |  | [1, 4] | upper | 2050 | -0.15
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Steam generation increases equipment cost by [MEUR/MW] | MEUR/MW | 2025 |  | [1, 4] | ctrl | 2025 | 0.2
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Steam generation increases equipment cost by [MEUR/MW] | MEUR/MW | 2025 |  | [1, 4] | ctrl | 2030 | 0.15
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Steam generation increases equipment cost by [MEUR/MW] | MEUR/MW | 2025 |  | [1, 4] | ctrl | 2035 | 0.1
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Steam generation increases equipment cost by [MEUR/MW] | MEUR/MW | 2025 |  | [1, 4] | ctrl | 2040 | 0.1
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Steam generation increases equipment cost by [MEUR/MW] | MEUR/MW | 2025 |  | [1, 4] | ctrl | 2050 | 0.1
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Steam generation increases equipment cost by [MEUR/MW] | MEUR/MW | 2025 |  | [1, 4] | lower | 2025 | 0.05
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Steam generation increases equipment cost by [MEUR/MW] | MEUR/MW | 2025 |  | [1, 4] | lower | 2050 | 0.05
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Steam generation increases equipment cost by [MEUR/MW] | MEUR/MW | 2025 |  | [1, 4] | upper | 2025 | 0.3
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Steam generation increases equipment cost by [MEUR/MW] | MEUR/MW | 2025 |  | [1, 4] | upper | 2050 | 0.2
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 100 K | pct. |  |  | [1, 4] | ctrl | 2025 | 2.05
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 100 K | pct. |  |  | [1, 4] | ctrl | 2030 | 2.1
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 100 K | pct. |  |  | [1, 4] | ctrl | 2035 | 2.15
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 100 K | pct. |  |  | [1, 4] | ctrl | 2040 | 2.2
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 100 K | pct. |  |  | [1, 4] | ctrl | 2050 | 2.2
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 100 K | pct. |  |  | [1, 4] | lower | 2025 | 1.7
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 100 K | pct. |  |  | [1, 4] | lower | 2050 | 1.9
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 100 K | pct. |  |  | [1, 4] | upper | 2025 | 2.85
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 100 K | pct. |  |  | [1, 4] | upper | 2050 | 3.2
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 40 K | pct. |  |  | [1, 4] | ctrl | 2025 | 4.45
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 40 K | pct. |  |  | [1, 4] | ctrl | 2030 | 4.65
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 40 K | pct. |  |  | [1, 4] | ctrl | 2035 | 4.7
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 40 K | pct. |  |  | [1, 4] | ctrl | 2040 | 4.8
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 40 K | pct. |  |  | [1, 4] | ctrl | 2050 | 4.9
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 40 K | pct. |  |  | [1, 4] | lower | 2025 | 3.65
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 40 K | pct. |  |  | [1, 4] | lower | 2050 | 4.05
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 40 K | pct. |  |  | [1, 4] | upper | 2025 | 6.5
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 40 K | pct. |  |  | [1, 4] | upper | 2050 | 7.3
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 80 K | pct. |  |  | [1, 4] | ctrl | 2025 | 2.4
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 80 K | pct. |  |  | [1, 4] | ctrl | 2030 | 2.45
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 80 K | pct. |  |  | [1, 4] | ctrl | 2035 | 2.5
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 80 K | pct. |  |  | [1, 4] | ctrl | 2040 | 2.55
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 80 K | pct. |  |  | [1, 4] | ctrl | 2050 | 2.6
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 80 K | pct. |  |  | [1, 4] | lower | 2025 | 2
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 80 K | pct. |  |  | [1, 4] | lower | 2050 | 2.2
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 80 K | pct. |  |  | [1, 4] | upper | 2025 | 3.4
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 80 K | pct. |  |  | [1, 4] | upper | 2050 | 3.8
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | Indirect investment cost [M€/MW] | M€/MW |  | I |  | ctrl | 2025 | 0.23
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | Indirect investment cost [M€/MW] | M€/MW |  | I |  | ctrl | 2030 | 0.23
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | Indirect investment cost [M€/MW] | M€/MW |  | I |  | ctrl | 2035 | 0.23
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | Indirect investment cost [M€/MW] | M€/MW |  | I |  | ctrl | 2040 | 0.23
2.a High temp. hp Up to 125C | High-temperature heat pumps up to 125 °C | Technology-specific data | Indirect investment cost [M€/MW] | M€/MW |  | I |  | ctrl | 2050 | 0.23
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 1 | ctrl | 2025 | 0.02
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 1 | ctrl | 2030 | 0.02
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 1 | ctrl | 2035 | 0.02
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 1 | ctrl | 2040 | 0.02
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 1 | ctrl | 2050 | 0.02
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 1 | lower | 2025 | 0.01
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 1 | lower | 2050 | 0.01
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 1 | upper | 2025 | 0.07
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 1 | upper | 2050 | 0.07
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Construction time [years] | years |  | E | 4 | ctrl | 2025 | 0.6
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Construction time [years] | years |  | E | 4 | ctrl | 2030 | 0.5
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Construction time [years] | years |  | E | 4 | ctrl | 2035 | 0.4
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Construction time [years] | years |  | E | 4 | ctrl | 2040 | 0.4
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Construction time [years] | years |  | E | 4 | ctrl | 2050 | 0.4
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Construction time [years] | years |  | E | 4 | lower | 2025 | 0.4
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Construction time [years] | years |  | E | 4 | lower | 2050 | 0.2
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Construction time [years] | years |  | E | 4 | upper | 2025 | 0.8
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Construction time [years] | years |  | E | 4 | upper | 2050 | 0.8
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Forced outage [days] | days |  |  | 4 | ctrl | 2025 | 0
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Forced outage [days] | days |  |  | 4 | ctrl | 2030 | 0
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Forced outage [days] | days |  |  | 4 | ctrl | 2035 | 0
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Forced outage [days] | days |  |  | 4 | ctrl | 2040 | 0
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Forced outage [days] | days |  |  | 4 | ctrl | 2050 | 0
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Forced outage [days] | days |  |  | 4 | lower | 2025 | 0
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Forced outage [days] | days |  |  | 4 | lower | 2050 | 0
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Forced outage [days] | days |  |  | 4 | upper | 2025 | 1
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Forced outage [days] | days |  |  | 4 | upper | 2050 | 1
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | B | 4 | ctrl | 2025 | 2
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | B | 4 | ctrl | 2030 | 2
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | B | 4 | ctrl | 2035 | 3
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | B | 4 | ctrl | 2040 | 3
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | B | 4 | ctrl | 2050 | 3
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | B | 4 | lower | 2025 | 0.5
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | B | 4 | lower | 2050 | 0.5
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | B | 4 | upper | 2025 | 80
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | B | 4 | upper | 2050 | 100
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 4 | ctrl | 2025 | 0.5
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 4 | ctrl | 2030 | 0.5
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 4 | ctrl | 2035 | 0.5
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 4 | ctrl | 2040 | 0.5
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 4 | ctrl | 2050 | 0.5
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 4 | lower | 2025 | 0
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 4 | lower | 2050 | 0
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 4 | upper | 2025 | 1
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 4 | upper | 2050 | 1
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2025 | 0.03
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2030 | 0.03
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2035 | 0.03
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2040 | 0.03
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | ctrl | 2050 | 0.03
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2025 | 0.02
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | lower | 2050 | 0.01
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2025 | 0.06
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  |  | upper | 2050 | 0.05
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Technical lifetime [years] | years |  | D | 4 | ctrl | 2025 | 20
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Technical lifetime [years] | years |  | D | 4 | ctrl | 2030 | 20
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Technical lifetime [years] | years |  | D | 4 | ctrl | 2035 | 20
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Technical lifetime [years] | years |  | D | 4 | ctrl | 2040 | 20
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Technical lifetime [years] | years |  | D | 4 | ctrl | 2050 | 20
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Technical lifetime [years] | years |  | D | 4 | lower | 2025 | 15
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Technical lifetime [years] | years |  | D | 4 | lower | 2050 | 15
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Technical lifetime [years] | years |  | D | 4 | upper | 2025 | 30
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Technical lifetime [years] | years |  | D | 4 | upper | 2050 | 30
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  |  | ctrl | 2025 | 2.7
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  |  | ctrl | 2030 | 2.8
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  |  | ctrl | 2035 | 2.85
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  |  | ctrl | 2040 | 2.9
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  |  | ctrl | 2050 | 2.95
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  |  | lower | 2025 | 2.2
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  |  | lower | 2050 | 2.45
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  |  | upper | 2025 | 3.95
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  |  | upper | 2050 | 4.45
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Total efficiency, net [%], nominel load. Based on a temperature lift of 65 K | pct. |  | C, H | 1 | ctrl | 2025 | 2.75
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Total efficiency, net [%], nominel load. Based on a temperature lift of 65 K | pct. |  | C, H | 1 | ctrl | 2030 | 2.85
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Total efficiency, net [%], nominel load. Based on a temperature lift of 65 K | pct. |  | C, H | 1 | ctrl | 2035 | 2.9
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Total efficiency, net [%], nominel load. Based on a temperature lift of 65 K | pct. |  | C, H | 1 | ctrl | 2040 | 2.95
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Total efficiency, net [%], nominel load. Based on a temperature lift of 65 K | pct. |  | C, H | 1 | ctrl | 2050 | 3
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Total efficiency, net [%], nominel load. Based on a temperature lift of 65 K | pct. |  | C, H | 1 | lower | 2025 | 2.25
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Total efficiency, net [%], nominel load. Based on a temperature lift of 65 K | pct. |  | C, H | 1 | lower | 2050 | 2.5
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Total efficiency, net [%], nominel load. Based on a temperature lift of 65 K | pct. |  | C, H | 1 | upper | 2025 | 4
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Energy/technical data | Total efficiency, net [%], nominel load. Based on a temperature lift of 65 K | pct. |  | C, H | 1 | upper | 2050 | 4.5
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | - of which equipment [%] | pct. |  | A | 1 | ctrl | 2025 | 0.4
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | - of which equipment [%] | pct. |  | A | 1 | ctrl | 2030 | 0.4
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | - of which equipment [%] | pct. |  | A | 1 | ctrl | 2035 | 0.4
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | - of which equipment [%] | pct. |  | A | 1 | ctrl | 2040 | 0.4
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | - of which equipment [%] | pct. |  | A | 1 | ctrl | 2050 | 0.4
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | - of which equipment [%] | pct. |  | A | 1 | lower | 2025 | 0.25
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | - of which equipment [%] | pct. |  | A | 1 | lower | 2050 | 0.25
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | - of which equipment [%] | pct. |  | A | 1 | upper | 2025 | 0.6
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | - of which equipment [%] | pct. |  | A | 1 | upper | 2050 | 0.7
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | - of which installation [%] | pct. |  | A | 3 | ctrl | 2025 | 0.6
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | - of which installation [%] | pct. |  | A | 3 | ctrl | 2030 | 0.6
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | - of which installation [%] | pct. |  | A | 3 | ctrl | 2035 | 0.6
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | - of which installation [%] | pct. |  | A | 3 | ctrl | 2040 | 0.6
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | - of which installation [%] | pct. |  | A | 3 | ctrl | 2050 | 0.6
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | - of which installation [%] | pct. |  | A | 3 | lower | 2025 | 0.4
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | - of which installation [%] | pct. |  | A | 3 | lower | 2050 | 0.3
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | - of which installation [%] | pct. |  | A | 3 | upper | 2025 | 0.75
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | - of which installation [%] | pct. |  | A | 3 | upper | 2050 | 0.75
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | Fixed O&M [EUR/MW_y], from last update in 2019 | EUR/MW_y | 2025 |  | 2 | ctrl | 2025 | 2494
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | Fixed O&M [EUR/MW_y], from last update in 2019 | EUR/MW_y | 2025 |  | 2 | ctrl | 2030 | 2456
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | Fixed O&M [EUR/MW_y], from last update in 2019 | EUR/MW_y | 2025 |  | 2 | ctrl | 2035 | 2382
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | Fixed O&M [EUR/MW_y], from last update in 2019 | EUR/MW_y | 2025 |  | 2 | ctrl | 2040 | 2382
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | Fixed O&M [EUR/MW_y], from last update in 2019 | EUR/MW_y | 2025 |  | 2 | ctrl | 2050 | 2345
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | Nominal investment (*total) [MEUR/MW] | MEUR/MW | 2025 | G |  | ctrl | 2025 | 1.55
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | Nominal investment (*total) [MEUR/MW] | MEUR/MW | 2025 | G |  | ctrl | 2030 | 1.5
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | Nominal investment (*total) [MEUR/MW] | MEUR/MW | 2025 | G |  | ctrl | 2035 | 1.45
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | Nominal investment (*total) [MEUR/MW] | MEUR/MW | 2025 | G |  | ctrl | 2040 | 1.4
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | Nominal investment (*total) [MEUR/MW] | MEUR/MW | 2025 | G |  | ctrl | 2050 | 1.35
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | Nominal investment (*total) [MEUR/MW] | MEUR/MW | 2025 | G |  | lower | 2025 | 1.25
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | Nominal investment (*total) [MEUR/MW] | MEUR/MW | 2025 | G |  | lower | 2050 | 1.1
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | Nominal investment (*total) [MEUR/MW] | MEUR/MW | 2025 | G |  | upper | 2025 | 1.8
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | Nominal investment (*total) [MEUR/MW] | MEUR/MW | 2025 | G |  | upper | 2050 | 1.65
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | Variable O&M [EUR/MWh], from last update in 2019 | EUR/MWh | 2025 |  | 1 | ctrl | 2025 | 3.6
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | Variable O&M [EUR/MWh], from last update in 2019 | EUR/MWh | 2025 |  | 1 | ctrl | 2030 | 3.54
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | Variable O&M [EUR/MWh], from last update in 2019 | EUR/MWh | 2025 |  | 1 | ctrl | 2035 | 3.43
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | Variable O&M [EUR/MWh], from last update in 2019 | EUR/MWh | 2025 |  | 1 | ctrl | 2040 | 3.43
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Financial data | Variable O&M [EUR/MWh], from last update in 2019 | EUR/MWh | 2025 |  | 1 | ctrl | 2050 | 3.39
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Cold start-up time [hours] | hours |  |  | 4 | ctrl | 2025 | 1
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Cold start-up time [hours] | hours |  |  | 4 | ctrl | 2030 | 1
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Cold start-up time [hours] | hours |  |  | 4 | ctrl | 2035 | 1
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Cold start-up time [hours] | hours |  |  | 4 | ctrl | 2040 | 1
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Cold start-up time [hours] | hours |  |  | 4 | ctrl | 2050 | 1
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Cold start-up time [hours] | hours |  |  | 4 | lower | 2025 | 0.5
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Cold start-up time [hours] | hours |  |  | 4 | lower | 2050 | 0.5
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Cold start-up time [hours] | hours |  |  | 4 | upper | 2025 | 1.5
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Cold start-up time [hours] | hours |  |  | 4 | upper | 2050 | 1.5
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Minimum load (of full load) [] |  |  | F | 4 | ctrl | 2025 | 0.25
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Minimum load (of full load) [] |  |  | F | 4 | ctrl | 2030 | 0.25
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Minimum load (of full load) [] |  |  | F | 4 | ctrl | 2035 | 0.25
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Minimum load (of full load) [] |  |  | F | 4 | ctrl | 2040 | 0.25
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Minimum load (of full load) [] |  |  | F | 4 | ctrl | 2050 | 0.25
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Minimum load (of full load) [] |  |  | F | 4 | lower | 2025 | 0.1
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Minimum load (of full load) [] |  |  | F | 4 | lower | 2050 | 0.1
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Minimum load (of full load) [] |  |  | F | 4 | upper | 2025 | 0.5
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Minimum load (of full load) [] |  |  | F | 4 | upper | 2050 | 0.5
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2025 | 0.05
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2030 | 0.07
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2035 | 0.08
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2040 | 0.09
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | ctrl | 2050 | 0.1
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2025 | 0.02
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | lower | 2050 | 0.05
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2025 | 0.1
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Primary regulation (of full load, per 30 seconds) [] |  |  |  |  | upper | 2050 | 0.2
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | ctrl | 2025 | 0.1
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | ctrl | 2030 | 0.14
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | ctrl | 2035 | 0.16
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | ctrl | 2040 | 0.18
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | ctrl | 2050 | 0.2
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | lower | 2025 | 0.04
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | lower | 2050 | 0.1
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | upper | 2025 | 0.2
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Secondary regulation (of full load, per minute) [] |  |  |  |  | upper | 2050 | 0.4
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Warm start-up time [hours] | hours |  |  | 4 | ctrl | 2025 | 0.25
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Warm start-up time [hours] | hours |  |  | 4 | ctrl | 2030 | 0.25
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Warm start-up time [hours] | hours |  |  | 4 | ctrl | 2035 | 0.25
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Warm start-up time [hours] | hours |  |  | 4 | ctrl | 2040 | 0.25
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Warm start-up time [hours] | hours |  |  | 4 | ctrl | 2050 | 0.25
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Warm start-up time [hours] | hours |  |  | 4 | lower | 2025 | 0.1
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Warm start-up time [hours] | hours |  |  | 4 | lower | 2050 | 0.1
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Warm start-up time [hours] | hours |  |  | 4 | upper | 2025 | 0.5
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Regulation ability | Warm start-up time [hours] | hours |  |  | 4 | upper | 2050 | 0.25
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Additional equipment cost for temperature lift above 75 K [MEUR/MW] | MEUR/MW | 2025 |  | [1, 4] | ctrl | 2025 | 0.2
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Additional equipment cost for temperature lift above 75 K [MEUR/MW] | MEUR/MW | 2025 |  | [1, 4] | ctrl | 2030 | 0.2
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Additional equipment cost for temperature lift above 75 K [MEUR/MW] | MEUR/MW | 2025 |  | [1, 4] | ctrl | 2035 | 0.15
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Additional equipment cost for temperature lift above 75 K [MEUR/MW] | MEUR/MW | 2025 |  | [1, 4] | ctrl | 2040 | 0.15
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Additional equipment cost for temperature lift above 75 K [MEUR/MW] | MEUR/MW | 2025 |  | [1, 4] | ctrl | 2050 | 0.15
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Additional equipment cost for temperature lift above 75 K [MEUR/MW] | MEUR/MW | 2025 |  | [1, 4] | lower | 2025 | 0.1
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Additional equipment cost for temperature lift above 75 K [MEUR/MW] | MEUR/MW | 2025 |  | [1, 4] | lower | 2050 | 0.1
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Additional equipment cost for temperature lift above 75 K [MEUR/MW] | MEUR/MW | 2025 |  | [1, 4] | upper | 2025 | 0.3
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Additional equipment cost for temperature lift above 75 K [MEUR/MW] | MEUR/MW | 2025 |  | [1, 4] | upper | 2050 | 0.35
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Steam generation decreases COP [%-point] | pct.-point |  |  | [1, 4] | ctrl | 2025 | -0.15
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Steam generation decreases COP [%-point] | pct.-point |  |  | [1, 4] | ctrl | 2030 | -0.1
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Steam generation decreases COP [%-point] | pct.-point |  |  | [1, 4] | ctrl | 2035 | -0.05
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Steam generation decreases COP [%-point] | pct.-point |  |  | [1, 4] | ctrl | 2040 | -0.05
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Steam generation decreases COP [%-point] | pct.-point |  |  | [1, 4] | ctrl | 2050 | -0.05
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Steam generation decreases COP [%-point] | pct.-point |  |  | [1, 4] | lower | 2025 | -0.05
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Steam generation decreases COP [%-point] | pct.-point |  |  | [1, 4] | lower | 2050 | -0.05
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Steam generation decreases COP [%-point] | pct.-point |  |  | [1, 4] | upper | 2025 | -0.2
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Steam generation decreases COP [%-point] | pct.-point |  |  | [1, 4] | upper | 2050 | -0.15
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Steam generation increases equipment cost by [MEUR/MW] | MEUR/MW | 2025 |  | [1, 4] | ctrl | 2025 | 0.2
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Steam generation increases equipment cost by [MEUR/MW] | MEUR/MW | 2025 |  | [1, 4] | ctrl | 2030 | 0.15
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Steam generation increases equipment cost by [MEUR/MW] | MEUR/MW | 2025 |  | [1, 4] | ctrl | 2035 | 0.1
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Steam generation increases equipment cost by [MEUR/MW] | MEUR/MW | 2025 |  | [1, 4] | ctrl | 2040 | 0.1
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Steam generation increases equipment cost by [MEUR/MW] | MEUR/MW | 2025 |  | [1, 4] | ctrl | 2050 | 0.1
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Steam generation increases equipment cost by [MEUR/MW] | MEUR/MW | 2025 |  | [1, 4] | lower | 2025 | 0.05
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Steam generation increases equipment cost by [MEUR/MW] | MEUR/MW | 2025 |  | [1, 4] | lower | 2050 | 0.05
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Steam generation increases equipment cost by [MEUR/MW] | MEUR/MW | 2025 |  | [1, 4] | upper | 2025 | 0.3
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Steam generation increases equipment cost by [MEUR/MW] | MEUR/MW | 2025 |  | [1, 4] | upper | 2050 | 0.2
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 100 K | pct. |  |  | [1, 4] | ctrl | 2025 | 2.05
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 100 K | pct. |  |  | [1, 4] | ctrl | 2030 | 2.1
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 100 K | pct. |  |  | [1, 4] | ctrl | 2035 | 2.15
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 100 K | pct. |  |  | [1, 4] | ctrl | 2040 | 2.2
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 100 K | pct. |  |  | [1, 4] | ctrl | 2050 | 2.2
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 100 K | pct. |  |  | [1, 4] | lower | 2025 | 1.7
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 100 K | pct. |  |  | [1, 4] | lower | 2050 | 1.9
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 100 K | pct. |  |  | [1, 4] | upper | 2025 | 2.85
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 100 K | pct. |  |  | [1, 4] | upper | 2050 | 3.2
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 40 K | pct. |  |  | [1, 4] | ctrl | 2025 | 4.45
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 40 K | pct. |  |  | [1, 4] | ctrl | 2030 | 4.65
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 40 K | pct. |  |  | [1, 4] | ctrl | 2035 | 4.7
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 40 K | pct. |  |  | [1, 4] | ctrl | 2040 | 4.8
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 40 K | pct. |  |  | [1, 4] | ctrl | 2050 | 4.9
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 40 K | pct. |  |  | [1, 4] | lower | 2025 | 3.65
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 40 K | pct. |  |  | [1, 4] | lower | 2050 | 4.05
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 40 K | pct. |  |  | [1, 4] | upper | 2025 | 6.5
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 40 K | pct. |  |  | [1, 4] | upper | 2050 | 7.3
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 80 K | pct. |  |  | [1, 4] | ctrl | 2025 | 2.4
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 80 K | pct. |  |  | [1, 4] | ctrl | 2030 | 2.45
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 80 K | pct. |  |  | [1, 4] | ctrl | 2035 | 2.5
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 80 K | pct. |  |  | [1, 4] | ctrl | 2040 | 2.55
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 80 K | pct. |  |  | [1, 4] | ctrl | 2050 | 2.6
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 80 K | pct. |  |  | [1, 4] | lower | 2025 | 2
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 80 K | pct. |  |  | [1, 4] | lower | 2050 | 2.2
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 80 K | pct. |  |  | [1, 4] | upper | 2025 | 3.4
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | - Total efficiency, net [%], nominel load. Based on a temperature lift of 80 K | pct. |  |  | [1, 4] | upper | 2050 | 3.8
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | Indirect investment cost [M€/MW] | M€/MW |  | I |  | ctrl | 2025 | 0.23
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | Indirect investment cost [M€/MW] | M€/MW |  | I |  | ctrl | 2030 | 0.23
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | Indirect investment cost [M€/MW] | M€/MW |  | I |  | ctrl | 2035 | 0.23
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | Indirect investment cost [M€/MW] | M€/MW |  | I |  | ctrl | 2040 | 0.23
2.b High temp. hp Up to 150 | High-temperature heat pumps up to 150 °C | Technology-specific data | Indirect investment cost [M€/MW] | M€/MW |  | I |  | ctrl | 2050 | 0.23
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 3 | ctrl | 2025 | 0.01
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 3 | ctrl | 2030 | 0.01
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 3 | ctrl | 2035 | 0.01
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 3 | ctrl | 2040 | 0.01
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 3 | ctrl | 2050 | 0.01
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 3 | lower | 2025 | 0
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 3 | lower | 2050 | 0
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 3 | upper | 2025 | 0.02
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 3 | upper | 2050 | 0.02
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Construction time [years] | years |  |  | [1, 3] | ctrl | 2025 | 0.1
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Construction time [years] | years |  |  | [1, 3] | ctrl | 2030 | 0.1
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Construction time [years] | years |  |  | [1, 3] | ctrl | 2035 | 0.1
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Construction time [years] | years |  |  | [1, 3] | ctrl | 2040 | 0.1
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Construction time [years] | years |  |  | [1, 3] | ctrl | 2050 | 0.1
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Construction time [years] | years |  |  | [1, 3] | lower | 2025 | 0.05
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Construction time [years] | years |  |  | [1, 3] | lower | 2050 | 0.05
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Construction time [years] | years |  |  | [1, 3] | upper | 2025 | 0.2
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Construction time [years] | years |  |  | [1, 3] | upper | 2050 | 0.2
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Forced outage [%] | pct. |  |  | 2 | ctrl | 2025 | 0
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Forced outage [%] | pct. |  |  | 2 | ctrl | 2030 | 0
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Forced outage [%] | pct. |  |  | 2 | ctrl | 2035 | 0
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Forced outage [%] | pct. |  |  | 2 | ctrl | 2040 | 0
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Forced outage [%] | pct. |  |  | 2 | ctrl | 2050 | 0
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Forced outage [%] | pct. |  |  | 2 | lower | 2025 | 0
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Forced outage [%] | pct. |  |  | 2 | lower | 2050 | 0
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Forced outage [%] | pct. |  |  | 2 | upper | 2025 | 0.01
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Forced outage [%] | pct. |  |  | 2 | upper | 2050 | 0.01
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A | 1 | ctrl | 2025 | 20
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A | 1 | ctrl | 2030 | 20
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A | 1 | ctrl | 2035 | 20
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A | 1 | ctrl | 2040 | 20
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A | 1 | ctrl | 2050 | 20
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A | 1 | lower | 2025 | 5
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A | 1 | lower | 2050 | 5
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A | 1 | upper | 2025 | 50
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A | 1 | upper | 2050 | 50
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | ctrl | 2025 | 0.5
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | ctrl | 2030 | 0.5
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | ctrl | 2035 | 0.5
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | ctrl | 2040 | 0.5
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | ctrl | 2050 | 0.5
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | lower | 2025 | 0
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | lower | 2050 | 0
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | upper | 2025 | 1
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | upper | 2050 | 1
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 2] | ctrl | 2025 | 25
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 2] | ctrl | 2030 | 25
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 2] | ctrl | 2035 | 25
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 2] | ctrl | 2040 | 25
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 2] | ctrl | 2050 | 25
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 2] | lower | 2025 | 15
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 2] | lower | 2050 | 15
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 2] | upper | 2025 | 35
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Technical lifetime [years] | years |  |  | [1, 2] | upper | 2050 | 35
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  |  | ctrl | 2025 | 12.1
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  |  | ctrl | 2030 | 12.7
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  |  | ctrl | 2035 | 13
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  |  | ctrl | 2040 | 13.3
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  |  | ctrl | 2050 | 13.8
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  |  | lower | 2025 | 9.5
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  |  | lower | 2050 | 10.06
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  |  | upper | 2025 | 14.62
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  |  | upper | 2050 | 16.66
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | B | 1 | ctrl | 2025 | 12.6
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | B | 1 | ctrl | 2030 | 13.2
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | B | 1 | ctrl | 2035 | 13.5
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | B | 1 | ctrl | 2040 | 13.8
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | B | 1 | ctrl | 2050 | 14.3
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | B | 1 | lower | 2025 | 10
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | B | 1 | lower | 2050 | 10.56
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | B | 1 | upper | 2025 | 15.12
4 MVR 5 K | Mechanical vapor recompression | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | B | 1 | upper | 2050 | 17.16
4 MVR 5 K | Mechanical vapor recompression | Financial data | - of which equipment [%] | pct. |  |  | [1, 5] | ctrl | 2025 | 0.6
4 MVR 5 K | Mechanical vapor recompression | Financial data | - of which equipment [%] | pct. |  |  | [1, 5] | ctrl | 2030 | 0.6
4 MVR 5 K | Mechanical vapor recompression | Financial data | - of which equipment [%] | pct. |  |  | [1, 5] | ctrl | 2035 | 0.6
4 MVR 5 K | Mechanical vapor recompression | Financial data | - of which equipment [%] | pct. |  |  | [1, 5] | ctrl | 2040 | 0.6
4 MVR 5 K | Mechanical vapor recompression | Financial data | - of which equipment [%] | pct. |  |  | [1, 5] | ctrl | 2050 | 0.6
4 MVR 5 K | Mechanical vapor recompression | Financial data | - of which installation [%] | pct. |  |  | [1, 5] | ctrl | 2025 | 0.4
4 MVR 5 K | Mechanical vapor recompression | Financial data | - of which installation [%] | pct. |  |  | [1, 5] | ctrl | 2030 | 0.4
4 MVR 5 K | Mechanical vapor recompression | Financial data | - of which installation [%] | pct. |  |  | [1, 5] | ctrl | 2035 | 0.4
4 MVR 5 K | Mechanical vapor recompression | Financial data | - of which installation [%] | pct. |  |  | [1, 5] | ctrl | 2040 | 0.4
4 MVR 5 K | Mechanical vapor recompression | Financial data | - of which installation [%] | pct. |  |  | [1, 5] | ctrl | 2050 | 0.4
4 MVR 5 K | Mechanical vapor recompression | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | 2 | ctrl | 2025 | 2345
4 MVR 5 K | Mechanical vapor recompression | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | 2 | ctrl | 2030 | 2345
4 MVR 5 K | Mechanical vapor recompression | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | 2 | ctrl | 2035 | 2345
4 MVR 5 K | Mechanical vapor recompression | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | 2 | ctrl | 2040 | 2345
4 MVR 5 K | Mechanical vapor recompression | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | 2 | ctrl | 2050 | 2345
4 MVR 5 K | Mechanical vapor recompression | Financial data | Nominal investment [M€/MW] | M€/MW |  |  | [1, 5] | ctrl | 2025 | 0.41
4 MVR 5 K | Mechanical vapor recompression | Financial data | Nominal investment [M€/MW] | M€/MW |  |  | [1, 5] | ctrl | 2030 | 0.39
4 MVR 5 K | Mechanical vapor recompression | Financial data | Nominal investment [M€/MW] | M€/MW |  |  | [1, 5] | ctrl | 2035 | 0.39
4 MVR 5 K | Mechanical vapor recompression | Financial data | Nominal investment [M€/MW] | M€/MW |  |  | [1, 5] | ctrl | 2040 | 0.38
4 MVR 5 K | Mechanical vapor recompression | Financial data | Nominal investment [M€/MW] | M€/MW |  |  | [1, 5] | ctrl | 2050 | 0.36
4 MVR 5 K | Mechanical vapor recompression | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | 2 | ctrl | 2025 | 2.1
4 MVR 5 K | Mechanical vapor recompression | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | 2 | ctrl | 2030 | 2
4 MVR 5 K | Mechanical vapor recompression | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | 2 | ctrl | 2035 | 2
4 MVR 5 K | Mechanical vapor recompression | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | 2 | ctrl | 2040 | 2
4 MVR 5 K | Mechanical vapor recompression | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | 2 | ctrl | 2050 | 1.9
4 MVR 5 K | Mechanical vapor recompression | Regulation Ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2025 | 1
4 MVR 5 K | Mechanical vapor recompression | Regulation Ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2030 | 1
4 MVR 5 K | Mechanical vapor recompression | Regulation Ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2035 | 1
4 MVR 5 K | Mechanical vapor recompression | Regulation Ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2040 | 1
4 MVR 5 K | Mechanical vapor recompression | Regulation Ability | Cold start-up time [hours] | hours |  |  | 3 | ctrl | 2050 | 1
4 MVR 5 K | Mechanical vapor recompression | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 4 | ctrl | 2025 | 0.15
4 MVR 5 K | Mechanical vapor recompression | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 4 | ctrl | 2030 | 0.15
4 MVR 5 K | Mechanical vapor recompression | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 4 | ctrl | 2035 | 0.15
4 MVR 5 K | Mechanical vapor recompression | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 4 | ctrl | 2040 | 0.15
4 MVR 5 K | Mechanical vapor recompression | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 4 | ctrl | 2050 | 0.15
4 MVR 5 K | Mechanical vapor recompression | Regulation Ability | Warm start-up time [hours] | hours |  |  | 3 | ctrl | 2025 | 0.5
4 MVR 5 K | Mechanical vapor recompression | Regulation Ability | Warm start-up time [hours] | hours |  |  | 3 | ctrl | 2030 | 0.5
4 MVR 5 K | Mechanical vapor recompression | Regulation Ability | Warm start-up time [hours] | hours |  |  | 3 | ctrl | 2035 | 0.5
4 MVR 5 K | Mechanical vapor recompression | Regulation Ability | Warm start-up time [hours] | hours |  |  | 3 | ctrl | 2040 | 0.5
4 MVR 5 K | Mechanical vapor recompression | Regulation Ability | Warm start-up time [hours] | hours |  |  | 3 | ctrl | 2050 | 0.5
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | ctrl | 2025 | 0.005
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | ctrl | 2030 | 0.005
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | ctrl | 2035 | 0.005
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | ctrl | 2040 | 0.005
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | ctrl | 2050 | 0.005
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | lower | 2025 | 0.001
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | lower | 2050 | 0.001
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | upper | 2025 | 0.005
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | upper | 2050 | 0.005
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2025 | 0.5
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 0.5
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2035 | 0.5
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2040 | 0.5
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 0.5
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2025 | 0.5
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 0.5
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2025 | 1
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 1
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Forced outage [%] | pct. |  |  | [1, 2] | ctrl | 2025 | 0.01
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Forced outage [%] | pct. |  |  | [1, 2] | ctrl | 2030 | 0.01
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Forced outage [%] | pct. |  |  | [1, 2] | ctrl | 2035 | 0.01
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Forced outage [%] | pct. |  |  | [1, 2] | ctrl | 2040 | 0.01
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Forced outage [%] | pct. |  |  | [1, 2] | ctrl | 2050 | 0.01
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Forced outage [%] | pct. |  |  | [1, 2] | lower | 2025 | 0.005
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Forced outage [%] | pct. |  |  | [1, 2] | lower | 2050 | 0.005
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Forced outage [%] | pct. |  |  | [1, 2] | upper | 2025 | 0.01
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Forced outage [%] | pct. |  |  | [1, 2] | upper | 2050 | 0.01
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A |  | ctrl | 2025 | 2
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A |  | ctrl | 2030 | 2
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A |  | ctrl | 2035 | 2
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A |  | ctrl | 2040 | 2
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A |  | ctrl | 2050 | 2
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A |  | lower | 2025 | 1
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A |  | lower | 2050 | 1
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A |  | upper | 2025 | 5
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A |  | upper | 2050 | 5
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | ctrl | 2025 | 0.2
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | ctrl | 2030 | 0.2
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | ctrl | 2035 | 0.2
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | ctrl | 2040 | 0.2
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | ctrl | 2050 | 0.2
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | lower | 2025 | 0.2
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | lower | 2050 | 0.2
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | upper | 2025 | 0.2
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | upper | 2050 | 0.2
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | ctrl | 2025 | 25
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | ctrl | 2030 | 25
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | ctrl | 2035 | 25
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | ctrl | 2040 | 25
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | ctrl | 2050 | 25
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | lower | 2025 | 20
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | lower | 2050 | 20
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | upper | 2025 | 25
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | upper | 2050 | 25
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  | [1, 2] | ctrl | 2025 | 0.99
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  | [1, 2] | ctrl | 2030 | 0.99
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  | [1, 2] | ctrl | 2035 | 0.99
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  | [1, 2] | ctrl | 2040 | 0.99
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  | [1, 2] | ctrl | 2050 | 0.99
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  | [1, 2] | lower | 2025 | 0.98
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  | [1, 2] | lower | 2050 | 0.98
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  | [1, 2] | upper | 2025 | 0.99
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  | [1, 2] | upper | 2050 | 0.99
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  |  | [1, 2] | ctrl | 2025 | 0.99
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  |  | [1, 2] | ctrl | 2030 | 0.99
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  |  | [1, 2] | ctrl | 2035 | 0.99
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  |  | [1, 2] | ctrl | 2040 | 0.99
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  |  | [1, 2] | ctrl | 2050 | 0.99
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  |  | [1, 2] | lower | 2025 | 0.98
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  |  | [1, 2] | lower | 2050 | 0.98
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  |  | [1, 2] | upper | 2025 | 1
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  |  | [1, 2] | upper | 2050 | 1
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Financial data | - of which equipment [%] | pct. |  |  | [2, 4] | ctrl | 2025 | 0.75
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Financial data | - of which equipment [%] | pct. |  |  | [2, 4] | ctrl | 2030 | 0.75
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Financial data | - of which equipment [%] | pct. |  |  | [2, 4] | ctrl | 2035 | 0.75
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Financial data | - of which equipment [%] | pct. |  |  | [2, 4] | ctrl | 2040 | 0.75
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Financial data | - of which equipment [%] | pct. |  |  | [2, 4] | ctrl | 2050 | 0.75
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Financial data | - of which installation [%] | pct. |  |  | [2, 4] | ctrl | 2025 | 0.25
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Financial data | - of which installation [%] | pct. |  |  | [2, 4] | ctrl | 2030 | 0.25
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Financial data | - of which installation [%] | pct. |  |  | [2, 4] | ctrl | 2035 | 0.25
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Financial data | - of which installation [%] | pct. |  |  | [2, 4] | ctrl | 2040 | 0.25
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Financial data | - of which installation [%] | pct. |  |  | [2, 4] | ctrl | 2050 | 0.25
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | [2, 3, 4] | ctrl | 2025 | 1442
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | [2, 3, 4] | ctrl | 2030 | 1375
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | [2, 3, 4] | ctrl | 2035 | 1341
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | [2, 3, 4] | ctrl | 2040 | 1307
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | [2, 3, 4] | ctrl | 2050 | 1240
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Financial data | Nominal investment [M€/MW] | M€/MW |  | B,C | [1, 2, 4] | ctrl | 2025 | 0.25
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Financial data | Nominal investment [M€/MW] | M€/MW |  | B,C | [1, 2, 4] | ctrl | 2030 | 0.22
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Financial data | Nominal investment [M€/MW] | M€/MW |  | B,C | [1, 2, 4] | ctrl | 2035 | 0.22
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Financial data | Nominal investment [M€/MW] | M€/MW |  | B,C | [1, 2, 4] | ctrl | 2040 | 0.22
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Financial data | Nominal investment [M€/MW] | M€/MW |  | B,C | [1, 2, 4] | ctrl | 2050 | 0.22
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | [2, 3, 4] | ctrl | 2025 | 0.674
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | [2, 3, 4] | ctrl | 2030 | 0.642
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | [2, 3, 4] | ctrl | 2035 | 0.627
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | [2, 3, 4] | ctrl | 2040 | 0.611
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | [2, 3, 4] | ctrl | 2050 | 0.578
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Regulation Ability | Cold start-up time [hours] | hours |  |  | 2 | ctrl | 2025 | 0.17
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Regulation Ability | Cold start-up time [hours] | hours |  |  | 2 | ctrl | 2030 | 0.17
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Regulation Ability | Cold start-up time [hours] | hours |  |  | 2 | ctrl | 2035 | 0.17
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Regulation Ability | Cold start-up time [hours] | hours |  |  | 2 | ctrl | 2040 | 0.17
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Regulation Ability | Cold start-up time [hours] | hours |  |  | 2 | ctrl | 2050 | 0.17
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 2 | ctrl | 2025 | 0.02
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 2 | ctrl | 2030 | 0.02
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 2 | ctrl | 2035 | 0.02
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 2 | ctrl | 2040 | 0.02
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 2 | ctrl | 2050 | 0.02
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Regulation Ability | Warm start-up time [hours] | hours |  |  | 2 | ctrl | 2025 | 0.03
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Regulation Ability | Warm start-up time [hours] | hours |  |  | 2 | ctrl | 2030 | 0.03
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Regulation Ability | Warm start-up time [hours] | hours |  |  | 2 | ctrl | 2035 | 0.03
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Regulation Ability | Warm start-up time [hours] | hours |  |  | 2 | ctrl | 2040 | 0.03
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Regulation Ability | Warm start-up time [hours] | hours |  |  | 2 | ctrl | 2050 | 0.03
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Technology-specific data | Additional investments cost for 12-16 bar boilers [M€/MW] | M€/MW |  |  |  | ctrl | 2025 | 0.064
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Technology-specific data | Additional investments cost for 12-16 bar boilers [M€/MW] | M€/MW |  |  |  | ctrl | 2030 | 0.057
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Technology-specific data | Additional investments cost for 12-16 bar boilers [M€/MW] | M€/MW |  |  |  | ctrl | 2035 | 0.057
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Technology-specific data | Additional investments cost for 12-16 bar boilers [M€/MW] | M€/MW |  |  |  | ctrl | 2040 | 0.057
5.1a Electric boiler steam | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar | Technology-specific data | Additional investments cost for 12-16 bar boilers [M€/MW] | M€/MW |  |  |  | ctrl | 2050 | 0.057
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | ctrl | 2025 | 0.005
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | ctrl | 2030 | 0.005
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | ctrl | 2035 | 0.005
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | ctrl | 2040 | 0.005
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | ctrl | 2050 | 0.005
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | lower | 2025 | 0.001
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | lower | 2050 | 0.001
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | upper | 2025 | 0.005
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | upper | 2050 | 0.005
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2025 | 0.5
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 0.5
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2035 | 0.5
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2040 | 0.5
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 0.5
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2025 | 0.5
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 0.5
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2025 | 1
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 1
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Forced outage [%] | pct. |  |  | [1, 2] | ctrl | 2025 | 0.01
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Forced outage [%] | pct. |  |  | [1, 2] | ctrl | 2030 | 0.01
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Forced outage [%] | pct. |  |  | [1, 2] | ctrl | 2035 | 0.01
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Forced outage [%] | pct. |  |  | [1, 2] | ctrl | 2040 | 0.01
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Forced outage [%] | pct. |  |  | [1, 2] | ctrl | 2050 | 0.01
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Forced outage [%] | pct. |  |  | [1, 2] | lower | 2025 | 0.005
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Forced outage [%] | pct. |  |  | [1, 2] | lower | 2050 | 0.005
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Forced outage [%] | pct. |  |  | [1, 2] | upper | 2025 | 0.01
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Forced outage [%] | pct. |  |  | [1, 2] | upper | 2050 | 0.01
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A |  | ctrl | 2025 | 15
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A |  | ctrl | 2030 | 15
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A |  | ctrl | 2035 | 15
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A |  | ctrl | 2040 | 15
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A |  | ctrl | 2050 | 15
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A |  | lower | 2025 | 5
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A |  | lower | 2050 | 5
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A |  | upper | 2025 | 60
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A |  | upper | 2050 | 60
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | ctrl | 2025 | 0.2
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | ctrl | 2030 | 0.2
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | ctrl | 2035 | 0.2
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | ctrl | 2040 | 0.2
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | ctrl | 2050 | 0.2
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | lower | 2025 | 0.2
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | lower | 2050 | 0.2
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | upper | 2025 | 0.2
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | upper | 2050 | 0.2
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | ctrl | 2025 | 25
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | ctrl | 2030 | 25
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | ctrl | 2035 | 25
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | ctrl | 2040 | 25
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | ctrl | 2050 | 25
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | lower | 2025 | 20
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | lower | 2050 | 20
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | upper | 2025 | 25
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | upper | 2050 | 25
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  | [1, 2] | ctrl | 2025 | 0.99
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  | [1, 2] | ctrl | 2030 | 0.99
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  | [1, 2] | ctrl | 2035 | 0.99
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  | [1, 2] | ctrl | 2040 | 0.99
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  | [1, 2] | ctrl | 2050 | 0.99
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  | [1, 2] | lower | 2025 | 0.98
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  | [1, 2] | lower | 2050 | 0.98
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  | [1, 2] | upper | 2025 | 0.99
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  | [1, 2] | upper | 2050 | 0.99
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  |  | [1, 2] | ctrl | 2025 | 0.99
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  |  | [1, 2] | ctrl | 2030 | 0.99
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  |  | [1, 2] | ctrl | 2035 | 0.99
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  |  | [1, 2] | ctrl | 2040 | 0.99
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  |  | [1, 2] | ctrl | 2050 | 0.99
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  |  | [1, 2] | lower | 2025 | 0.98
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  |  | [1, 2] | lower | 2050 | 0.98
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  |  | [1, 2] | upper | 2025 | 1
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  |  | [1, 2] | upper | 2050 | 1
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Financial data | - of which equipment [%] | pct. |  |  | 2 | ctrl | 2025 | 0.85
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Financial data | - of which equipment [%] | pct. |  |  | 2 | ctrl | 2030 | 0.85
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Financial data | - of which equipment [%] | pct. |  |  | 2 | ctrl | 2035 | 0.85
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Financial data | - of which equipment [%] | pct. |  |  | 2 | ctrl | 2040 | 0.85
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Financial data | - of which equipment [%] | pct. |  |  | 2 | ctrl | 2050 | 0.85
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Financial data | - of which installation [%] | pct. |  |  | 2 | ctrl | 2025 | 0.15
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Financial data | - of which installation [%] | pct. |  |  | 2 | ctrl | 2030 | 0.15
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Financial data | - of which installation [%] | pct. |  |  | 2 | ctrl | 2035 | 0.15
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Financial data | - of which installation [%] | pct. |  |  | 2 | ctrl | 2040 | 0.15
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Financial data | - of which installation [%] | pct. |  |  | 2 | ctrl | 2050 | 0.15
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | [2, 3, 4] | ctrl | 2025 | 1298
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | [2, 3, 4] | ctrl | 2030 | 1237
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | [2, 3, 4] | ctrl | 2035 | 1208
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | [2, 3, 4] | ctrl | 2040 | 1177
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | [2, 3, 4] | ctrl | 2050 | 1116
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Financial data | Nominal investment [M€/MW] | M€/MW |  | B,C | [1, 2, 4] | ctrl | 2025 | 0.11
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Financial data | Nominal investment [M€/MW] | M€/MW |  | B,C | [1, 2, 4] | ctrl | 2030 | 0.1
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Financial data | Nominal investment [M€/MW] | M€/MW |  | B,C | [1, 2, 4] | ctrl | 2035 | 0.1
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Financial data | Nominal investment [M€/MW] | M€/MW |  | B,C | [1, 2, 4] | ctrl | 2040 | 0.1
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Financial data | Nominal investment [M€/MW] | M€/MW |  | B,C | [1, 2, 4] | ctrl | 2050 | 0.1
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | [2, 3, 4] | ctrl | 2025 | 0.61
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | [2, 3, 4] | ctrl | 2030 | 0.58
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | [2, 3, 4] | ctrl | 2035 | 0.56
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | [2, 3, 4] | ctrl | 2040 | 0.55
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | [2, 3, 4] | ctrl | 2050 | 0.52
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Regulation Ability | Cold start-up time [hours] | hours |  |  | 2 | ctrl | 2025 | 0.17
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Regulation Ability | Cold start-up time [hours] | hours |  |  | 2 | ctrl | 2030 | 0.17
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Regulation Ability | Cold start-up time [hours] | hours |  |  | 2 | ctrl | 2035 | 0.17
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Regulation Ability | Cold start-up time [hours] | hours |  |  | 2 | ctrl | 2040 | 0.17
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Regulation Ability | Cold start-up time [hours] | hours |  |  | 2 | ctrl | 2050 | 0.17
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 2 | ctrl | 2025 | 0.02
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 2 | ctrl | 2030 | 0.02
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 2 | ctrl | 2035 | 0.02
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 2 | ctrl | 2040 | 0.02
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 2 | ctrl | 2050 | 0.02
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Regulation Ability | Warm start-up time [hours] | hours |  |  | 2 | ctrl | 2025 | 0.03
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Regulation Ability | Warm start-up time [hours] | hours |  |  | 2 | ctrl | 2030 | 0.03
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Regulation Ability | Warm start-up time [hours] | hours |  |  | 2 | ctrl | 2035 | 0.03
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Regulation Ability | Warm start-up time [hours] | hours |  |  | 2 | ctrl | 2040 | 0.03
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Regulation Ability | Warm start-up time [hours] | hours |  |  | 2 | ctrl | 2050 | 0.03
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Technology-specific data | Additional investments cost for 12-16 bar boilers [M€/MW] | M€/MW |  |  |  | ctrl | 2025 | 0.021
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Technology-specific data | Additional investments cost for 12-16 bar boilers [M€/MW] | M€/MW |  |  |  | ctrl | 2030 | 0.018
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Technology-specific data | Additional investments cost for 12-16 bar boilers [M€/MW] | M€/MW |  |  |  | ctrl | 2035 | 0.018
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Technology-specific data | Additional investments cost for 12-16 bar boilers [M€/MW] | M€/MW |  |  |  | ctrl | 2040 | 0.018
5.1b Electric boiler steam | Electric boiler, 10 kV, steam, 1-12 bar | Technology-specific data | Additional investments cost for 12-16 bar boilers [M€/MW] | M€/MW |  |  |  | ctrl | 2050 | 0.018
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | ctrl | 2025 | 0.005
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | ctrl | 2030 | 0.005
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | ctrl | 2035 | 0.005
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | ctrl | 2040 | 0.005
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | ctrl | 2050 | 0.005
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | lower | 2025 | 0.001
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | lower | 2050 | 0.001
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | upper | 2025 | 0.005
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | upper | 2050 | 0.005
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2025 | 0.5
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 0.5
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2035 | 0.5
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2040 | 0.5
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 0.5
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2025 | 0.5
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 0.5
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2025 | 1
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 1
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Forced outage [%] | pct. |  |  | [1, 2] | ctrl | 2025 | 0.01
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Forced outage [%] | pct. |  |  | [1, 2] | ctrl | 2030 | 0.01
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Forced outage [%] | pct. |  |  | [1, 2] | ctrl | 2035 | 0.01
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Forced outage [%] | pct. |  |  | [1, 2] | ctrl | 2040 | 0.01
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Forced outage [%] | pct. |  |  | [1, 2] | ctrl | 2050 | 0.01
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Forced outage [%] | pct. |  |  | [1, 2] | lower | 2025 | 0.005
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Forced outage [%] | pct. |  |  | [1, 2] | lower | 2050 | 0.005
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Forced outage [%] | pct. |  |  | [1, 2] | upper | 2025 | 0.01
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Forced outage [%] | pct. |  |  | [1, 2] | upper | 2050 | 0.01
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A |  | ctrl | 2025 | 2
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A |  | ctrl | 2030 | 2
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A |  | ctrl | 2035 | 2
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A |  | ctrl | 2040 | 2
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A |  | ctrl | 2050 | 2
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A |  | lower | 2025 | 1
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A |  | lower | 2050 | 1
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A |  | upper | 2025 | 5
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A |  | upper | 2050 | 5
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 1 | ctrl | 2025 | 0.2
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 1 | ctrl | 2030 | 0.2
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 1 | ctrl | 2035 | 0.2
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 1 | ctrl | 2040 | 0.2
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 1 | ctrl | 2050 | 0.2
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 1 | lower | 2025 | 0.2
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 1 | lower | 2050 | 0.2
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 1 | upper | 2025 | 0.2
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 1 | upper | 2050 | 0.2
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | ctrl | 2025 | 25
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | ctrl | 2030 | 25
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | ctrl | 2035 | 25
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | ctrl | 2040 | 25
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | ctrl | 2050 | 25
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | lower | 2025 | 20
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | lower | 2050 | 20
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | upper | 2025 | 25
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | upper | 2050 | 25
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  | [1, 2] | ctrl | 2025 | 0.99
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  | [1, 2] | ctrl | 2030 | 0.99
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  | [1, 2] | ctrl | 2035 | 0.99
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  | [1, 2] | ctrl | 2040 | 0.99
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  | [1, 2] | ctrl | 2050 | 0.99
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  | [1, 2] | lower | 2025 | 0.98
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  | [1, 2] | lower | 2050 | 0.98
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  | [1, 2] | upper | 2025 | 0.99
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  | [1, 2] | upper | 2050 | 0.99
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  |  | [1, 2] | ctrl | 2025 | 0.99
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  |  | [1, 2] | ctrl | 2030 | 0.99
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  |  | [1, 2] | ctrl | 2035 | 0.99
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  |  | [1, 2] | ctrl | 2040 | 0.99
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  |  | [1, 2] | ctrl | 2050 | 0.99
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  |  | [1, 2] | lower | 2025 | 0.98
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  |  | [1, 2] | lower | 2050 | 0.98
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  |  | [1, 2] | upper | 2025 | 1
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  |  | [1, 2] | upper | 2050 | 1
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Financial data | - of which equipment [%] | pct. |  |  | 2 | ctrl | 2025 | 0.75
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Financial data | - of which equipment [%] | pct. |  |  | 2 | ctrl | 2030 | 0.75
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Financial data | - of which equipment [%] | pct. |  |  | 2 | ctrl | 2035 | 0.75
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Financial data | - of which equipment [%] | pct. |  |  | 2 | ctrl | 2040 | 0.75
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Financial data | - of which equipment [%] | pct. |  |  | 2 | ctrl | 2050 | 0.75
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Financial data | - of which installation [%] | pct. |  |  | 2 | ctrl | 2025 | 0.25
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Financial data | - of which installation [%] | pct. |  |  | 2 | ctrl | 2030 | 0.25
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Financial data | - of which installation [%] | pct. |  |  | 2 | ctrl | 2035 | 0.25
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Financial data | - of which installation [%] | pct. |  |  | 2 | ctrl | 2040 | 0.25
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Financial data | - of which installation [%] | pct. |  |  | 2 | ctrl | 2050 | 0.25
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | 1 | ctrl | 2025 | 1254
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | 1 | ctrl | 2030 | 1196
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | 1 | ctrl | 2035 | 1166
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | 1 | ctrl | 2040 | 1137
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | 1 | ctrl | 2050 | 1079
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Financial data | Nominal investment [M€/MW] | M€/MW |  | B,C | [1, 2, 4] | ctrl | 2025 | 0.202
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Financial data | Nominal investment [M€/MW] | M€/MW |  | B,C | [1, 2, 4] | ctrl | 2030 | 0.187
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Financial data | Nominal investment [M€/MW] | M€/MW |  | B,C | [1, 2, 4] | ctrl | 2035 | 0.187
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Financial data | Nominal investment [M€/MW] | M€/MW |  | B,C | [1, 2, 4] | ctrl | 2040 | 0.187
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Financial data | Nominal investment [M€/MW] | M€/MW |  | B,C | [1, 2, 4] | ctrl | 2050 | 0.187
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | [2, 3, 4] | ctrl | 2025 | 0.59
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | [2, 3, 4] | ctrl | 2030 | 0.56
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | [2, 3, 4] | ctrl | 2035 | 0.54
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | [2, 3, 4] | ctrl | 2040 | 0.53
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | [2, 3, 4] | ctrl | 2050 | 0.5
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Regulation Ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2025 | 0.08
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Regulation Ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 0.08
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Regulation Ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2035 | 0.08
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Regulation Ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2040 | 0.08
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Regulation Ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 0.08
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 1 | ctrl | 2025 | 0.05
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 1 | ctrl | 2030 | 0.05
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 1 | ctrl | 2035 | 0.05
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 1 | ctrl | 2040 | 0.05
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 1 | ctrl | 2050 | 0.05
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Regulation Ability | Warm start-up time [hours] | hours |  |  | 1 | ctrl | 2025 | 0.008
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Regulation Ability | Warm start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 0.008
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Regulation Ability | Warm start-up time [hours] | hours |  |  | 1 | ctrl | 2035 | 0.008
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Regulation Ability | Warm start-up time [hours] | hours |  |  | 1 | ctrl | 2040 | 0.008
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Regulation Ability | Warm start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 0.008
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Technology-specific data | Additional investments cost for 12-16 bar boilers [M€/MW] | M€/MW |  |  |  | ctrl | 2025 | 0.057
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Technology-specific data | Additional investments cost for 12-16 bar boilers [M€/MW] | M€/MW |  |  |  | ctrl | 2030 | 0.049
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Technology-specific data | Additional investments cost for 12-16 bar boilers [M€/MW] | M€/MW |  |  |  | ctrl | 2035 | 0.049
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Technology-specific data | Additional investments cost for 12-16 bar boilers [M€/MW] | M€/MW |  |  |  | ctrl | 2040 | 0.049
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Technology-specific data | Additional investments cost for 12-16 bar boilers [M€/MW] | M€/MW |  |  |  | ctrl | 2050 | 0.049
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Technology-specific data | Indirect investments cost [M€/MW] | M€/MW |  | D |  | ctrl | 2025 | 0.101
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Technology-specific data | Indirect investments cost [M€/MW] | M€/MW |  | D |  | ctrl | 2030 | 0.0935
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Technology-specific data | Indirect investments cost [M€/MW] | M€/MW |  | D |  | ctrl | 2035 | 0.0935
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Technology-specific data | Indirect investments cost [M€/MW] | M€/MW |  | D |  | ctrl | 2040 | 0.0935
5.2a Electric boiler hot wate | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar | Technology-specific data | Indirect investments cost [M€/MW] | M€/MW |  | D |  | ctrl | 2050 | 0.0935
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | ctrl | 2025 | 0.005
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | ctrl | 2030 | 0.005
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | ctrl | 2035 | 0.005
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | ctrl | 2040 | 0.005
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | ctrl | 2050 | 0.005
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | lower | 2025 | 0.001
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | lower | 2050 | 0.001
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | upper | 2025 | 0.005
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | upper | 2050 | 0.005
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2025 | 0.5
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 0.5
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2035 | 0.5
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2040 | 0.5
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 0.5
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2025 | 0.5
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 0.5
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2025 | 1
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 1
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Forced outage [%] | pct. |  |  | [1, 2] | ctrl | 2025 | 0.01
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Forced outage [%] | pct. |  |  | [1, 2] | ctrl | 2030 | 0.01
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Forced outage [%] | pct. |  |  | [1, 2] | ctrl | 2035 | 0.01
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Forced outage [%] | pct. |  |  | [1, 2] | ctrl | 2040 | 0.01
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Forced outage [%] | pct. |  |  | [1, 2] | ctrl | 2050 | 0.01
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Forced outage [%] | pct. |  |  | [1, 2] | lower | 2025 | 0.005
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Forced outage [%] | pct. |  |  | [1, 2] | lower | 2050 | 0.005
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Forced outage [%] | pct. |  |  | [1, 2] | upper | 2025 | 0.01
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Forced outage [%] | pct. |  |  | [1, 2] | upper | 2050 | 0.01
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A |  | ctrl | 2025 | 15
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A |  | ctrl | 2030 | 15
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A |  | ctrl | 2035 | 15
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A |  | ctrl | 2040 | 15
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A |  | ctrl | 2050 | 15
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A |  | lower | 2025 | 5
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A |  | lower | 2050 | 5
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A |  | upper | 2025 | 60
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  | A |  | upper | 2050 | 60
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 1 | ctrl | 2025 | 0.2
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 1 | ctrl | 2030 | 0.2
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 1 | ctrl | 2035 | 0.2
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 1 | ctrl | 2040 | 0.2
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 1 | ctrl | 2050 | 0.2
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 1 | lower | 2025 | 0.2
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 1 | lower | 2050 | 0.2
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 1 | upper | 2025 | 0.2
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 1 | upper | 2050 | 0.2
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | ctrl | 2025 | 25
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | ctrl | 2030 | 25
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | ctrl | 2035 | 25
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | ctrl | 2040 | 25
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | ctrl | 2050 | 25
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | lower | 2025 | 20
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | lower | 2050 | 20
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | upper | 2025 | 25
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Technical lifetime [years] | years |  |  | 2 | upper | 2050 | 25
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  | [1, 2] | ctrl | 2025 | 0.99
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  | [1, 2] | ctrl | 2030 | 0.99
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  | [1, 2] | ctrl | 2035 | 0.99
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  | [1, 2] | ctrl | 2040 | 0.99
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  | [1, 2] | ctrl | 2050 | 0.99
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  | [1, 2] | lower | 2025 | 0.98
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  | [1, 2] | lower | 2050 | 0.98
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  | [1, 2] | upper | 2025 | 0.99
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Total efficiency, net [%], annual average | pct. |  |  | [1, 2] | upper | 2050 | 0.99
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  |  | [1, 2] | ctrl | 2025 | 0.99
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  |  | [1, 2] | ctrl | 2030 | 0.99
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  |  | [1, 2] | ctrl | 2035 | 0.99
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  |  | [1, 2] | ctrl | 2040 | 0.99
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  |  | [1, 2] | ctrl | 2050 | 0.99
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  |  | [1, 2] | lower | 2025 | 0.98
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  |  | [1, 2] | lower | 2050 | 0.98
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  |  | [1, 2] | upper | 2025 | 1
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  |  | [1, 2] | upper | 2050 | 1
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Financial data | - of which equipment [%] | pct. |  |  | 2 | ctrl | 2025 | 0.85
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Financial data | - of which equipment [%] | pct. |  |  | 2 | ctrl | 2030 | 0.85
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Financial data | - of which equipment [%] | pct. |  |  | 2 | ctrl | 2035 | 0.85
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Financial data | - of which equipment [%] | pct. |  |  | 2 | ctrl | 2040 | 0.85
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Financial data | - of which equipment [%] | pct. |  |  | 2 | ctrl | 2050 | 0.85
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Financial data | - of which installation [%] | pct. |  |  | 2 | ctrl | 2025 | 0.15
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Financial data | - of which installation [%] | pct. |  |  | 2 | ctrl | 2030 | 0.15
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Financial data | - of which installation [%] | pct. |  |  | 2 | ctrl | 2035 | 0.15
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Financial data | - of which installation [%] | pct. |  |  | 2 | ctrl | 2040 | 0.15
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Financial data | - of which installation [%] | pct. |  |  | 2 | ctrl | 2050 | 0.15
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | [1, 2, 4] | ctrl | 2025 | 1103
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | [1, 2, 4] | ctrl | 2030 | 1076
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | [1, 2, 4] | ctrl | 2035 | 1050
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | [1, 2, 4] | ctrl | 2040 | 1023
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  |  | [1, 2, 4] | ctrl | 2050 | 971
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Financial data | Nominal investment [M€/MW] | M€/MW |  | B,C | [1, 2, 4] | ctrl | 2025 | 0.089
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Financial data | Nominal investment [M€/MW] | M€/MW |  | B,C | [1, 2, 4] | ctrl | 2030 | 0.084
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Financial data | Nominal investment [M€/MW] | M€/MW |  | B,C | [1, 2, 4] | ctrl | 2035 | 0.084
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Financial data | Nominal investment [M€/MW] | M€/MW |  | B,C | [1, 2, 4] | ctrl | 2040 | 0.084
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Financial data | Nominal investment [M€/MW] | M€/MW |  | B,C | [1, 2, 4] | ctrl | 2050 | 0.084
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | [2, 3, 4] | ctrl | 2025 | 0.53
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | [2, 3, 4] | ctrl | 2030 | 0.5
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | [2, 3, 4] | ctrl | 2035 | 0.49
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | [2, 3, 4] | ctrl | 2040 | 0.48
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Financial data | Variable O&M [€/MWh] | €/MWh |  |  | [2, 3, 4] | ctrl | 2050 | 0.45
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Regulation Ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2025 | 0.08
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Regulation Ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 0.08
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Regulation Ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2035 | 0.08
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Regulation Ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2040 | 0.08
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Regulation Ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 0.08
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 1 | ctrl | 2025 | 0.05
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 1 | ctrl | 2030 | 0.05
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 1 | ctrl | 2035 | 0.05
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 1 | ctrl | 2040 | 0.05
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 1 | ctrl | 2050 | 0.05
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Regulation Ability | Warm start-up time [hours] | hours |  |  | 1 | ctrl | 2025 | 0.008
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Regulation Ability | Warm start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 0.008
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Regulation Ability | Warm start-up time [hours] | hours |  |  | 1 | ctrl | 2035 | 0.008
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Regulation Ability | Warm start-up time [hours] | hours |  |  | 1 | ctrl | 2040 | 0.008
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Regulation Ability | Warm start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 0.008
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Technology-specific data | Additional investments cost for 12-16 bar boilers [M€/MW] | M€/MW |  |  |  | ctrl | 2025 | 0.018
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Technology-specific data | Additional investments cost for 12-16 bar boilers [M€/MW] | M€/MW |  |  |  | ctrl | 2030 | 0.016
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Technology-specific data | Additional investments cost for 12-16 bar boilers [M€/MW] | M€/MW |  |  |  | ctrl | 2035 | 0.016
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Technology-specific data | Additional investments cost for 12-16 bar boilers [M€/MW] | M€/MW |  |  |  | ctrl | 2040 | 0.016
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Technology-specific data | Additional investments cost for 12-16 bar boilers [M€/MW] | M€/MW |  |  |  | ctrl | 2050 | 0.016
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Technology-specific data | Indirect investments cost [M€/MW] | M€/MW |  | D |  | ctrl | 2025 | 0.0445
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Technology-specific data | Indirect investments cost [M€/MW] | M€/MW |  | D |  | ctrl | 2030 | 0.042
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Technology-specific data | Indirect investments cost [M€/MW] | M€/MW |  | D |  | ctrl | 2035 | 0.042
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Technology-specific data | Indirect investments cost [M€/MW] | M€/MW |  | D |  | ctrl | 2040 | 0.042
5.2b Electric boiler hot wate | Electric boiler,10 kV, hot water, 1-12 bar | Technology-specific data | Indirect investments cost [M€/MW] | M€/MW |  | D |  | ctrl | 2050 | 0.042
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | ctrl | 2025 | 0.0015
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | ctrl | 2030 | 0.0015
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | ctrl | 2035 | 0.0015
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | ctrl | 2040 | 0.0015
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | ctrl | 2050 | 0.0015
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | lower | 2025 | 0
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | lower | 2050 | 0
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | upper | 2025 | 0.0015
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [1, 2] | upper | 2050 | 0.0015
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Construction time [years] | years |  |  | [1, 2] | ctrl | 2025 | 0.2
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Construction time [years] | years |  |  | [1, 2] | ctrl | 2030 | 0.2
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Construction time [years] | years |  |  | [1, 2] | ctrl | 2035 | 0.2
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Construction time [years] | years |  |  | [1, 2] | ctrl | 2040 | 0.2
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Construction time [years] | years |  |  | [1, 2] | ctrl | 2050 | 0.2
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Construction time [years] | years |  |  | [1, 2] | lower | 2025 | 0.02
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Construction time [years] | years |  |  | [1, 2] | lower | 2050 | 0.02
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Construction time [years] | years |  |  | [1, 2] | upper | 2025 | 0.7
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Construction time [years] | years |  |  | [1, 2] | upper | 2050 | 0.7
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Forced outage [%] | pct. |  |  | 1 | ctrl | 2025 | 0.01
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Forced outage [%] | pct. |  |  | 1 | ctrl | 2030 | 0.01
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Forced outage [%] | pct. |  |  | 1 | ctrl | 2035 | 0.01
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Forced outage [%] | pct. |  |  | 1 | ctrl | 2040 | 0.01
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Forced outage [%] | pct. |  |  | 1 | ctrl | 2050 | 0.01
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Forced outage [%] | pct. |  |  | 1 | lower | 2025 | 0
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Forced outage [%] | pct. |  |  | 1 | lower | 2050 | 0
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Forced outage [%] | pct. |  |  | 1 | upper | 2025 | 0.02
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Forced outage [%] | pct. |  |  | 1 | upper | 2050 | 0.02
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | [1, 2, 3, 6] | ctrl | 2025 | 5
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | [1, 2, 3, 6] | ctrl | 2030 | 5
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | [1, 2, 3, 6] | ctrl | 2035 | 5
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | [1, 2, 3, 6] | ctrl | 2040 | 5
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | [1, 2, 3, 6] | ctrl | 2050 | 5
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | [1, 2, 3, 6] | lower | 2025 | 0.5
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | [1, 2, 3, 6] | lower | 2050 | 0.5
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | [1, 2, 3, 6] | upper | 2025 | 50
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | [1, 2, 3, 6] | upper | 2050 | 50
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 2] | ctrl | 2025 | 0.5
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 2] | ctrl | 2030 | 0.5
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 2] | ctrl | 2035 | 0.5
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 2] | ctrl | 2040 | 0.5
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 2] | ctrl | 2050 | 0.5
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 2] | lower | 2025 | 0.3
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 2] | lower | 2050 | 0.3
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 2] | upper | 2025 | 0.6
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | [1, 2] | upper | 2050 | 0.6
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | [2, 3] | ctrl | 2025 | 0.008
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | [2, 3] | ctrl | 2030 | 0.008
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | [2, 3] | ctrl | 2035 | 0.008
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | [2, 3] | ctrl | 2040 | 0.008
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | [2, 3] | ctrl | 2050 | 0.008
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | [2, 3] | lower | 2025 | 0.007
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | [2, 3] | lower | 2050 | 0.007
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | [2, 3] | upper | 2025 | 0.01
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | [2, 3] | upper | 2050 | 0.01
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2025 | 25
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2035 | 25
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2040 | 25
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2025 | 25
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 25
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A, B, D | [1, 4] | ctrl | 2025 | 0.939
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A, B, D | [1, 4] | ctrl | 2030 | 0.939
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A, B, D | [1, 4] | ctrl | 2035 | 0.939
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A, B, D | [1, 4] | ctrl | 2040 | 0.939
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A, B, D | [1, 4] | ctrl | 2050 | 0.939
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A, B, D | [1, 4] | lower | 2025 | 0.919
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A, B, D | [1, 4] | lower | 2050 | 0.919
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A, B, D | [1, 4] | upper | 2025 | 0.949
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A, B, D | [1, 4] | upper | 2050 | 0.949
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A, B, E | [1, 4, 6] | ctrl | 2025 | 0.94
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A, B, E | [1, 4, 6] | ctrl | 2030 | 0.94
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A, B, E | [1, 4, 6] | ctrl | 2035 | 0.94
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A, B, E | [1, 4, 6] | ctrl | 2040 | 0.94
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A, B, E | [1, 4, 6] | ctrl | 2050 | 0.94
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A, B, E | [1, 4, 6] | lower | 2025 | 0.92
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A, B, E | [1, 4, 6] | lower | 2050 | 0.92
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A, B, E | [1, 4, 6] | upper | 2025 | 0.95
6.1 Boiler, gas and oil | Boiler, gas and oil | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A, B, E | [1, 4, 6] | upper | 2050 | 0.95
6.1 Boiler, gas and oil | Boiler, gas and oil | Financial data | - of which equipment [%] | pct. |  |  | [1, 2] | ctrl | 2025 | 0.66
6.1 Boiler, gas and oil | Boiler, gas and oil | Financial data | - of which equipment [%] | pct. |  |  | [1, 2] | ctrl | 2030 | 0.66
6.1 Boiler, gas and oil | Boiler, gas and oil | Financial data | - of which equipment [%] | pct. |  |  | [1, 2] | ctrl | 2035 | 0.66
6.1 Boiler, gas and oil | Boiler, gas and oil | Financial data | - of which equipment [%] | pct. |  |  | [1, 2] | ctrl | 2040 | 0.66
6.1 Boiler, gas and oil | Boiler, gas and oil | Financial data | - of which equipment [%] | pct. |  |  | [1, 2] | ctrl | 2050 | 0.66
6.1 Boiler, gas and oil | Boiler, gas and oil | Financial data | - of which installation [%] | pct. |  |  | [1, 2] | ctrl | 2025 | 0.34
6.1 Boiler, gas and oil | Boiler, gas and oil | Financial data | - of which installation [%] | pct. |  |  | [1, 2] | ctrl | 2030 | 0.34
6.1 Boiler, gas and oil | Boiler, gas and oil | Financial data | - of which installation [%] | pct. |  |  | [1, 2] | ctrl | 2035 | 0.34
6.1 Boiler, gas and oil | Boiler, gas and oil | Financial data | - of which installation [%] | pct. |  |  | [1, 2] | ctrl | 2040 | 0.34
6.1 Boiler, gas and oil | Boiler, gas and oil | Financial data | - of which installation [%] | pct. |  |  | [1, 2] | ctrl | 2050 | 0.34
6.1 Boiler, gas and oil | Boiler, gas and oil | Financial data | Fixed O&M [EUR/MW_y] | EUR/MW_y | 2025 |  | [1, 2] | ctrl | 2025 | 2000
6.1 Boiler, gas and oil | Boiler, gas and oil | Financial data | Fixed O&M [EUR/MW_y] | EUR/MW_y | 2025 |  | [1, 2] | ctrl | 2030 | 2000
6.1 Boiler, gas and oil | Boiler, gas and oil | Financial data | Fixed O&M [EUR/MW_y] | EUR/MW_y | 2025 |  | [1, 2] | ctrl | 2035 | 2000
6.1 Boiler, gas and oil | Boiler, gas and oil | Financial data | Fixed O&M [EUR/MW_y] | EUR/MW_y | 2025 |  | [1, 2] | ctrl | 2040 | 2000
6.1 Boiler, gas and oil | Boiler, gas and oil | Financial data | Fixed O&M [EUR/MW_y] | EUR/MW_y | 2025 |  | [1, 2] | ctrl | 2050 | 2000
6.1 Boiler, gas and oil | Boiler, gas and oil | Financial data | Nominal investment (*total) [MEUR/MW] | MEUR/MW | 2025 | C, B | [1, 2, 6] | ctrl | 2025 | 0.09
6.1 Boiler, gas and oil | Boiler, gas and oil | Financial data | Nominal investment (*total) [MEUR/MW] | MEUR/MW | 2025 | C, B | [1, 2, 6] | ctrl | 2030 | 0.09
6.1 Boiler, gas and oil | Boiler, gas and oil | Financial data | Nominal investment (*total) [MEUR/MW] | MEUR/MW | 2025 | C, B | [1, 2, 6] | ctrl | 2035 | 0.09
6.1 Boiler, gas and oil | Boiler, gas and oil | Financial data | Nominal investment (*total) [MEUR/MW] | MEUR/MW | 2025 | C, B | [1, 2, 6] | ctrl | 2040 | 0.09
6.1 Boiler, gas and oil | Boiler, gas and oil | Financial data | Nominal investment (*total) [MEUR/MW] | MEUR/MW | 2025 | C, B | [1, 2, 6] | ctrl | 2050 | 0.09
6.1 Boiler, gas and oil | Boiler, gas and oil | Financial data | Variable O&M [EUR/MWh] | EUR/MWh | 2025 |  | 1 | ctrl | 2025 | 1.23
6.1 Boiler, gas and oil | Boiler, gas and oil | Financial data | Variable O&M [EUR/MWh] | EUR/MWh | 2025 |  | 1 | ctrl | 2030 | 1.23
6.1 Boiler, gas and oil | Boiler, gas and oil | Financial data | Variable O&M [EUR/MWh] | EUR/MWh | 2025 |  | 1 | ctrl | 2035 | 1.23
6.1 Boiler, gas and oil | Boiler, gas and oil | Financial data | Variable O&M [EUR/MWh] | EUR/MWh | 2025 |  | 1 | ctrl | 2040 | 1.23
6.1 Boiler, gas and oil | Boiler, gas and oil | Financial data | Variable O&M [EUR/MWh] | EUR/MWh | 2025 |  | 1 | ctrl | 2050 | 1.23
6.1 Boiler, gas and oil | Boiler, gas and oil | Regulation ability | Cold start-up time [hours] | hours |  |  | [1, 2, 6] | ctrl | 2025 | 0.5
6.1 Boiler, gas and oil | Boiler, gas and oil | Regulation ability | Cold start-up time [hours] | hours |  |  | [1, 2, 6] | ctrl | 2030 | 0.5
6.1 Boiler, gas and oil | Boiler, gas and oil | Regulation ability | Cold start-up time [hours] | hours |  |  | [1, 2, 6] | ctrl | 2035 | 0.5
6.1 Boiler, gas and oil | Boiler, gas and oil | Regulation ability | Cold start-up time [hours] | hours |  |  | [1, 2, 6] | ctrl | 2040 | 0.5
6.1 Boiler, gas and oil | Boiler, gas and oil | Regulation ability | Cold start-up time [hours] | hours |  |  | [1, 2, 6] | ctrl | 2050 | 0.5
6.1 Boiler, gas and oil | Boiler, gas and oil | Regulation ability | Cold start-up time [hours] | hours |  |  | [1, 2, 6] | lower | 2025 | 0.3
6.1 Boiler, gas and oil | Boiler, gas and oil | Regulation ability | Cold start-up time [hours] | hours |  |  | [1, 2, 6] | upper | 2025 | 1
6.1 Boiler, gas and oil | Boiler, gas and oil | Regulation ability | Minimum load (of full load) [%] | pct. |  |  | [1, 2, 6] | ctrl | 2025 | 0.15
6.1 Boiler, gas and oil | Boiler, gas and oil | Regulation ability | Minimum load (of full load) [%] | pct. |  |  | [1, 2, 6] | ctrl | 2030 | 0.15
6.1 Boiler, gas and oil | Boiler, gas and oil | Regulation ability | Minimum load (of full load) [%] | pct. |  |  | [1, 2, 6] | ctrl | 2035 | 0.15
6.1 Boiler, gas and oil | Boiler, gas and oil | Regulation ability | Minimum load (of full load) [%] | pct. |  |  | [1, 2, 6] | ctrl | 2040 | 0.15
6.1 Boiler, gas and oil | Boiler, gas and oil | Regulation ability | Minimum load (of full load) [%] | pct. |  |  | [1, 2, 6] | ctrl | 2050 | 0.15
6.1 Boiler, gas and oil | Boiler, gas and oil | Regulation ability | Minimum load (of full load) [%] | pct. |  |  | [1, 2, 6] | lower | 2025 | 0.1
6.1 Boiler, gas and oil | Boiler, gas and oil | Regulation ability | Minimum load (of full load) [%] | pct. |  |  | [1, 2, 6] | upper | 2025 | 0.2
6.1 Boiler, gas and oil | Boiler, gas and oil | Regulation ability | Primary regulation (of full load, per 30 seconds) [%] | pct. |  | H | [1, 2, 6] | ctrl | 2025 | 0.15
6.1 Boiler, gas and oil | Boiler, gas and oil | Regulation ability | Primary regulation (of full load, per 30 seconds) [%] | pct. |  | H | [1, 2, 6] | ctrl | 2030 | 0.15
6.1 Boiler, gas and oil | Boiler, gas and oil | Regulation ability | Primary regulation (of full load, per 30 seconds) [%] | pct. |  | H | [1, 2, 6] | ctrl | 2035 | 0.15
6.1 Boiler, gas and oil | Boiler, gas and oil | Regulation ability | Primary regulation (of full load, per 30 seconds) [%] | pct. |  | H | [1, 2, 6] | ctrl | 2040 | 0.15
6.1 Boiler, gas and oil | Boiler, gas and oil | Regulation ability | Primary regulation (of full load, per 30 seconds) [%] | pct. |  | H | [1, 2, 6] | ctrl | 2050 | 0.15
6.1 Boiler, gas and oil | Boiler, gas and oil | Regulation ability | Primary regulation (of full load, per 30 seconds) [%] | pct. |  | H | [1, 2, 6] | lower | 2025 | 0.035
6.1 Boiler, gas and oil | Boiler, gas and oil | Regulation ability | Primary regulation (of full load, per 30 seconds) [%] | pct. |  | H | [1, 2, 6] | upper | 2025 | 0.3
6.1 Boiler, gas and oil | Boiler, gas and oil | Regulation ability | Secondary regulation (of full load, per minute) [%] | pct. |  | H | [1, 2, 6] | ctrl | 2025 | 0.3
6.1 Boiler, gas and oil | Boiler, gas and oil | Regulation ability | Secondary regulation (of full load, per minute) [%] | pct. |  | H | [1, 2, 6] | ctrl | 2030 | 0.3
6.1 Boiler, gas and oil | Boiler, gas and oil | Regulation ability | Secondary regulation (of full load, per minute) [%] | pct. |  | H | [1, 2, 6] | ctrl | 2035 | 0.3
6.1 Boiler, gas and oil | Boiler, gas and oil | Regulation ability | Secondary regulation (of full load, per minute) [%] | pct. |  | H | [1, 2, 6] | ctrl | 2040 | 0.3
6.1 Boiler, gas and oil | Boiler, gas and oil | Regulation ability | Secondary regulation (of full load, per minute) [%] | pct. |  | H | [1, 2, 6] | ctrl | 2050 | 0.3
6.1 Boiler, gas and oil | Boiler, gas and oil | Regulation ability | Secondary regulation (of full load, per minute) [%] | pct. |  | H | [1, 2, 6] | lower | 2025 | 0.07
6.1 Boiler, gas and oil | Boiler, gas and oil | Regulation ability | Secondary regulation (of full load, per minute) [%] | pct. |  | H | [1, 2, 6] | upper | 2025 | 0.6
6.1 Boiler, gas and oil | Boiler, gas and oil | Regulation ability | Warm start-up time [hours] | hours |  |  | [1, 2, 6] | ctrl | 2025 | 0.06
6.1 Boiler, gas and oil | Boiler, gas and oil | Regulation ability | Warm start-up time [hours] | hours |  |  | [1, 2, 6] | ctrl | 2030 | 0.06
6.1 Boiler, gas and oil | Boiler, gas and oil | Regulation ability | Warm start-up time [hours] | hours |  |  | [1, 2, 6] | ctrl | 2035 | 0.06
6.1 Boiler, gas and oil | Boiler, gas and oil | Regulation ability | Warm start-up time [hours] | hours |  |  | [1, 2, 6] | ctrl | 2040 | 0.06
6.1 Boiler, gas and oil | Boiler, gas and oil | Regulation ability | Warm start-up time [hours] | hours |  |  | [1, 2, 6] | ctrl | 2050 | 0.06
6.1 Boiler, gas and oil | Boiler, gas and oil | Regulation ability | Warm start-up time [hours] | hours |  |  | [1, 2, 6] | lower | 2025 | 0.025
6.1 Boiler, gas and oil | Boiler, gas and oil | Regulation ability | Warm start-up time [hours] | hours |  |  | [1, 2, 6] | upper | 2025 | 0.2
6.1 Boiler, gas and oil | Boiler, gas and oil | Technology-specific data | - Adding flue gas condenser (after economiser) increases efficiency by [%-point] (gas only) | pct.-point |  | I, E | [1, 2, 5] | ctrl | 2025 | 0.06
6.1 Boiler, gas and oil | Boiler, gas and oil | Technology-specific data | - Adding flue gas condenser (after economiser) increases efficiency by [%-point] (gas only) | pct.-point |  | I, E | [1, 2, 5] | ctrl | 2030 | 0.06
6.1 Boiler, gas and oil | Boiler, gas and oil | Technology-specific data | - Adding flue gas condenser (after economiser) increases efficiency by [%-point] (gas only) | pct.-point |  | I, E | [1, 2, 5] | ctrl | 2035 | 0.06
6.1 Boiler, gas and oil | Boiler, gas and oil | Technology-specific data | - Adding flue gas condenser (after economiser) increases efficiency by [%-point] (gas only) | pct.-point |  | I, E | [1, 2, 5] | ctrl | 2040 | 0.06
6.1 Boiler, gas and oil | Boiler, gas and oil | Technology-specific data | - Adding flue gas condenser (after economiser) increases efficiency by [%-point] (gas only) | pct.-point |  | I, E | [1, 2, 5] | ctrl | 2050 | 0.06
6.1 Boiler, gas and oil | Boiler, gas and oil | Technology-specific data | - Adding flue gas condenser (after economiser) increases nominal investment by [%] (gas only) | pct. |  | I | 2 | ctrl | 2025 | 0.1
6.1 Boiler, gas and oil | Boiler, gas and oil | Technology-specific data | - Adding flue gas condenser (after economiser) increases nominal investment by [%] (gas only) | pct. |  | I | 2 | ctrl | 2030 | 0.1
6.1 Boiler, gas and oil | Boiler, gas and oil | Technology-specific data | - Adding flue gas condenser (after economiser) increases nominal investment by [%] (gas only) | pct. |  | I | 2 | ctrl | 2035 | 0.1
6.1 Boiler, gas and oil | Boiler, gas and oil | Technology-specific data | - Adding flue gas condenser (after economiser) increases nominal investment by [%] (gas only) | pct. |  | I | 2 | ctrl | 2040 | 0.1
6.1 Boiler, gas and oil | Boiler, gas and oil | Technology-specific data | - Adding flue gas condenser (after economiser) increases nominal investment by [%] (gas only) | pct. |  | I | 2 | ctrl | 2050 | 0.1
6.1 Boiler, gas and oil | Boiler, gas and oil | Technology-specific data | - Hot water boiler instead of steam boiler increases efficiency by [%-point] | pct.-point |  | F |  | ctrl | 2025 | 0.01
6.1 Boiler, gas and oil | Boiler, gas and oil | Technology-specific data | - Hot water boiler instead of steam boiler increases efficiency by [%-point] | pct.-point |  | F |  | ctrl | 2030 | 0.01
6.1 Boiler, gas and oil | Boiler, gas and oil | Technology-specific data | - Hot water boiler instead of steam boiler increases efficiency by [%-point] | pct.-point |  | F |  | ctrl | 2035 | 0.01
6.1 Boiler, gas and oil | Boiler, gas and oil | Technology-specific data | - Hot water boiler instead of steam boiler increases efficiency by [%-point] | pct.-point |  | F |  | ctrl | 2040 | 0.01
6.1 Boiler, gas and oil | Boiler, gas and oil | Technology-specific data | - Hot water boiler instead of steam boiler increases efficiency by [%-point] | pct.-point |  | F |  | ctrl | 2050 | 0.01
6.1 Boiler, gas and oil | Boiler, gas and oil | Technology-specific data | - Hot water boiler instead of steam boiler reduces nominal investment by [%] | pct. |  | G | [2, 3] | ctrl | 2025 | 0.3
6.1 Boiler, gas and oil | Boiler, gas and oil | Technology-specific data | - Hot water boiler instead of steam boiler reduces nominal investment by [%] | pct. |  | G | [2, 3] | ctrl | 2030 | 0.3
6.1 Boiler, gas and oil | Boiler, gas and oil | Technology-specific data | - Hot water boiler instead of steam boiler reduces nominal investment by [%] | pct. |  | G | [2, 3] | ctrl | 2035 | 0.3
6.1 Boiler, gas and oil | Boiler, gas and oil | Technology-specific data | - Hot water boiler instead of steam boiler reduces nominal investment by [%] | pct. |  | G | [2, 3] | ctrl | 2040 | 0.3
6.1 Boiler, gas and oil | Boiler, gas and oil | Technology-specific data | - Hot water boiler instead of steam boiler reduces nominal investment by [%] | pct. |  | G | [2, 3] | ctrl | 2050 | 0.3
6.1 Boiler, gas and oil | Boiler, gas and oil | Technology-specific data | Indirect investment cost [M€/MW] | M€/MW |  | J | 2 | ctrl | 2025 | 0.23
6.1 Boiler, gas and oil | Boiler, gas and oil | Technology-specific data | Indirect investment cost [M€/MW] | M€/MW |  | J | 2 | ctrl | 2030 | 0.23
6.1 Boiler, gas and oil | Boiler, gas and oil | Technology-specific data | Indirect investment cost [M€/MW] | M€/MW |  | J | 2 | ctrl | 2035 | 0.23
6.1 Boiler, gas and oil | Boiler, gas and oil | Technology-specific data | Indirect investment cost [M€/MW] | M€/MW |  | J | 2 | ctrl | 2040 | 0.23
6.1 Boiler, gas and oil | Boiler, gas and oil | Technology-specific data | Indirect investment cost [M€/MW] | M€/MW |  | J | 2 | ctrl | 2050 | 0.23
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 1 | ctrl | 2025 | 0.02
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 1 | ctrl | 2030 | 0.02
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 1 | ctrl | 2035 | 0.02
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 1 | ctrl | 2040 | 0.02
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 1 | ctrl | 2050 | 0.02
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 1 | lower | 2025 | 0.02
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 1 | lower | 2050 | 0.02
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 1 | upper | 2025 | 0.02
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | 1 | upper | 2050 | 0.02
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2025 | 1
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 1
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2035 | 1
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2040 | 1
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 1
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2025 | 0.5
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Construction time [years] | years |  |  | 1 | lower | 2050 | 0.5
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2025 | 1.5
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Construction time [years] | years |  |  | 1 | upper | 2050 | 1.5
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Forced outage [%] | pct. |  |  | 1 | ctrl | 2025 | 0.03
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Forced outage [%] | pct. |  |  | 1 | ctrl | 2030 | 0.03
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Forced outage [%] | pct. |  |  | 1 | ctrl | 2035 | 0.03
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Forced outage [%] | pct. |  |  | 1 | ctrl | 2040 | 0.03
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Forced outage [%] | pct. |  |  | 1 | ctrl | 2050 | 0.03
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Forced outage [%] | pct. |  |  | 1 | lower | 2025 | 0.03
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Forced outage [%] | pct. |  |  | 1 | lower | 2050 | 0.03
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Forced outage [%] | pct. |  |  | 1 | upper | 2025 | 0.03
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Forced outage [%] | pct. |  |  | 1 | upper | 2050 | 0.03
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | [1, 4, 5] | ctrl | 2025 | 6.5
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | [1, 4, 5] | ctrl | 2030 | 6.5
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | [1, 4, 5] | ctrl | 2035 | 6.5
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | [1, 4, 5] | ctrl | 2040 | 6.5
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | [1, 4, 5] | ctrl | 2050 | 6.5
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | [1, 4, 5] | lower | 2025 | 0.3
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | [1, 4, 5] | lower | 2050 | 0.3
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | [1, 4, 5] | upper | 2025 | 50
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | [1, 4, 5] | upper | 2050 | 50
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 1 | ctrl | 2025 | 2
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 1 | ctrl | 2030 | 2
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 1 | ctrl | 2035 | 2
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 1 | ctrl | 2040 | 2
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 1 | ctrl | 2050 | 2
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 1 | lower | 2025 | 1.7
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 1 | lower | 2050 | 1.5
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 1 | upper | 2025 | 2.3
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 1 | upper | 2050 | 2.5
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2025 | 0.2
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2030 | 0.2
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2035 | 0.2
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2040 | 0.2
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | ctrl | 2050 | 0.2
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | lower | 2025 | 0.14
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | lower | 2050 | 0.12
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | upper | 2025 | 0.25
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 1 | upper | 2050 | 0.27
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2025 | 25
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2030 | 25
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2035 | 25
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2040 | 25
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | ctrl | 2050 | 25
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2025 | 20
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | lower | 2050 | 20
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2025 | 35
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Technical lifetime [years] | years |  |  | 1 | upper | 2050 | 35
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A, B, D | 2 | ctrl | 2025 | 0.889
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A, B, D | 2 | ctrl | 2030 | 0.889
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A, B, D | 2 | ctrl | 2035 | 0.889
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A, B, D | 2 | ctrl | 2040 | 0.889
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A, B, D | 2 | ctrl | 2050 | 0.889
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A, B, D | 2 | lower | 2025 | 0.869
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A, B, D | 2 | lower | 2050 | 0.869
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A, B, D | 2 | upper | 2025 | 0.909
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A, B, D | 2 | upper | 2050 | 0.909
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A, B | 2 | ctrl | 2025 | 0.89
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A, B | 2 | ctrl | 2030 | 0.89
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A, B | 2 | ctrl | 2035 | 0.89
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A, B | 2 | ctrl | 2040 | 0.89
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A, B | 2 | ctrl | 2050 | 0.89
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A, B | 2 | lower | 2025 | 0.87
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A, B | 2 | lower | 2050 | 0.87
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A, B | 2 | upper | 2025 | 0.91
6.2 Boiler, biomass | Boiler, biomass | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A, B | 2 | upper | 2050 | 0.91
6.2 Boiler, biomass | Boiler, biomass | Financial data | - of which equipment [%] | pct. |  |  | 1 | ctrl | 2025 | 0.6
6.2 Boiler, biomass | Boiler, biomass | Financial data | - of which equipment [%] | pct. |  |  | 1 | ctrl | 2030 | 0.6
6.2 Boiler, biomass | Boiler, biomass | Financial data | - of which equipment [%] | pct. |  |  | 1 | ctrl | 2035 | 0.6
6.2 Boiler, biomass | Boiler, biomass | Financial data | - of which equipment [%] | pct. |  |  | 1 | ctrl | 2040 | 0.6
6.2 Boiler, biomass | Boiler, biomass | Financial data | - of which equipment [%] | pct. |  |  | 1 | ctrl | 2050 | 0.6
6.2 Boiler, biomass | Boiler, biomass | Financial data | - of which installation [%] | pct. |  |  | 1 | ctrl | 2025 | 0.4
6.2 Boiler, biomass | Boiler, biomass | Financial data | - of which installation [%] | pct. |  |  | 1 | ctrl | 2030 | 0.4
6.2 Boiler, biomass | Boiler, biomass | Financial data | - of which installation [%] | pct. |  |  | 1 | ctrl | 2035 | 0.4
6.2 Boiler, biomass | Boiler, biomass | Financial data | - of which installation [%] | pct. |  |  | 1 | ctrl | 2040 | 0.4
6.2 Boiler, biomass | Boiler, biomass | Financial data | - of which installation [%] | pct. |  |  | 1 | ctrl | 2050 | 0.4
6.2 Boiler, biomass | Boiler, biomass | Financial data | Fixed O&M [EUR/MW_y] | EUR/MW_y | 2025 |  | 1 | ctrl | 2025 | 39500
6.2 Boiler, biomass | Boiler, biomass | Financial data | Fixed O&M [EUR/MW_y] | EUR/MW_y | 2025 |  | 1 | ctrl | 2030 | 38700
6.2 Boiler, biomass | Boiler, biomass | Financial data | Fixed O&M [EUR/MW_y] | EUR/MW_y | 2025 |  | 1 | ctrl | 2035 | 37900
6.2 Boiler, biomass | Boiler, biomass | Financial data | Fixed O&M [EUR/MW_y] | EUR/MW_y | 2025 |  | 1 | ctrl | 2040 | 37100
6.2 Boiler, biomass | Boiler, biomass | Financial data | Fixed O&M [EUR/MW_y] | EUR/MW_y | 2025 |  | 1 | ctrl | 2050 | 35600
6.2 Boiler, biomass | Boiler, biomass | Financial data | Nominal investment (*total) [MEUR/MW] | MEUR/MW | 2025 |  | 1 | ctrl | 2025 | 0.87841
6.2 Boiler, biomass | Boiler, biomass | Financial data | Nominal investment (*total) [MEUR/MW] | MEUR/MW | 2025 |  | 1 | ctrl | 2030 | 0.82892
6.2 Boiler, biomass | Boiler, biomass | Financial data | Nominal investment (*total) [MEUR/MW] | MEUR/MW | 2025 |  | 1 | ctrl | 2035 | 0.80727
6.2 Boiler, biomass | Boiler, biomass | Financial data | Nominal investment (*total) [MEUR/MW] | MEUR/MW | 2025 |  | 1 | ctrl | 2040 | 0.78562
6.2 Boiler, biomass | Boiler, biomass | Financial data | Nominal investment (*total) [MEUR/MW] | MEUR/MW | 2025 |  | 1 | ctrl | 2050 | 0.74232
6.2 Boiler, biomass | Boiler, biomass | Financial data | Variable O&M [EUR/MWh] | EUR/MWh | 2025 | C, H | 1 | ctrl | 2025 | 1.45
6.2 Boiler, biomass | Boiler, biomass | Financial data | Variable O&M [EUR/MWh] | EUR/MWh | 2025 | C, H | 1 | ctrl | 2030 | 1.45
6.2 Boiler, biomass | Boiler, biomass | Financial data | Variable O&M [EUR/MWh] | EUR/MWh | 2025 | C, H | 1 | ctrl | 2035 | 1.45
6.2 Boiler, biomass | Boiler, biomass | Financial data | Variable O&M [EUR/MWh] | EUR/MWh | 2025 | C, H | 1 | ctrl | 2040 | 1.45
6.2 Boiler, biomass | Boiler, biomass | Financial data | Variable O&M [EUR/MWh] | EUR/MWh | 2025 | C, H | 1 | ctrl | 2050 | 1.45
6.2 Boiler, biomass | Boiler, biomass | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2025 | 0.5
6.2 Boiler, biomass | Boiler, biomass | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 0.5
6.2 Boiler, biomass | Boiler, biomass | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2035 | 0.5
6.2 Boiler, biomass | Boiler, biomass | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2040 | 0.5
6.2 Boiler, biomass | Boiler, biomass | Regulation ability | Cold start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 0.5
6.2 Boiler, biomass | Boiler, biomass | Regulation ability | Minimum load (of full load) [%] | pct. |  |  | 1 | ctrl | 2025 | 0.2
6.2 Boiler, biomass | Boiler, biomass | Regulation ability | Minimum load (of full load) [%] | pct. |  |  | 1 | ctrl | 2030 | 0.2
6.2 Boiler, biomass | Boiler, biomass | Regulation ability | Minimum load (of full load) [%] | pct. |  |  | 1 | ctrl | 2035 | 0.2
6.2 Boiler, biomass | Boiler, biomass | Regulation ability | Minimum load (of full load) [%] | pct. |  |  | 1 | ctrl | 2040 | 0.2
6.2 Boiler, biomass | Boiler, biomass | Regulation ability | Minimum load (of full load) [%] | pct. |  |  | 1 | ctrl | 2050 | 0.2
6.2 Boiler, biomass | Boiler, biomass | Regulation ability | Secondary regulation (of full load, per minute) [%] | pct. |  |  | 1 | ctrl | 2025 | 0.1
6.2 Boiler, biomass | Boiler, biomass | Regulation ability | Secondary regulation (of full load, per minute) [%] | pct. |  |  | 1 | ctrl | 2030 | 0.1
6.2 Boiler, biomass | Boiler, biomass | Regulation ability | Secondary regulation (of full load, per minute) [%] | pct. |  |  | 1 | ctrl | 2035 | 0.1
6.2 Boiler, biomass | Boiler, biomass | Regulation ability | Secondary regulation (of full load, per minute) [%] | pct. |  |  | 1 | ctrl | 2040 | 0.1
6.2 Boiler, biomass | Boiler, biomass | Regulation ability | Secondary regulation (of full load, per minute) [%] | pct. |  |  | 1 | ctrl | 2050 | 0.1
6.2 Boiler, biomass | Boiler, biomass | Regulation ability | Warm start-up time [hours] | hours |  |  | 1 | ctrl | 2025 | 0.25
6.2 Boiler, biomass | Boiler, biomass | Regulation ability | Warm start-up time [hours] | hours |  |  | 1 | ctrl | 2030 | 0.25
6.2 Boiler, biomass | Boiler, biomass | Regulation ability | Warm start-up time [hours] | hours |  |  | 1 | ctrl | 2035 | 0.25
6.2 Boiler, biomass | Boiler, biomass | Regulation ability | Warm start-up time [hours] | hours |  |  | 1 | ctrl | 2040 | 0.25
6.2 Boiler, biomass | Boiler, biomass | Regulation ability | Warm start-up time [hours] | hours |  |  | 1 | ctrl | 2050 | 0.25
6.2 Boiler, biomass | Boiler, biomass | Technology-specific data | - Hot water boiler instead of steam boiler increases efficiency by [%-point] | pct.-point |  | G |  | ctrl | 2025 | 0.01
6.2 Boiler, biomass | Boiler, biomass | Technology-specific data | - Hot water boiler instead of steam boiler increases efficiency by [%-point] | pct.-point |  | G |  | ctrl | 2030 | 0.01
6.2 Boiler, biomass | Boiler, biomass | Technology-specific data | - Hot water boiler instead of steam boiler increases efficiency by [%-point] | pct.-point |  | G |  | ctrl | 2035 | 0.01
6.2 Boiler, biomass | Boiler, biomass | Technology-specific data | - Hot water boiler instead of steam boiler increases efficiency by [%-point] | pct.-point |  | G |  | ctrl | 2040 | 0.01
6.2 Boiler, biomass | Boiler, biomass | Technology-specific data | - Hot water boiler instead of steam boiler increases efficiency by [%-point] | pct.-point |  | G |  | ctrl | 2050 | 0.01
6.2 Boiler, biomass | Boiler, biomass | Technology-specific data | - Using wood chips, and adding flue gas condenser (after economiser) increases efficiency by [%-point] | pct.-point |  | F, E | [1, 3] | ctrl | 2025 | 0.25
6.2 Boiler, biomass | Boiler, biomass | Technology-specific data | - Using wood chips, and adding flue gas condenser (after economiser) increases efficiency by [%-point] | pct.-point |  | F, E | [1, 3] | ctrl | 2030 | 0.25
6.2 Boiler, biomass | Boiler, biomass | Technology-specific data | - Using wood chips, and adding flue gas condenser (after economiser) increases efficiency by [%-point] | pct.-point |  | F, E | [1, 3] | ctrl | 2035 | 0.25
6.2 Boiler, biomass | Boiler, biomass | Technology-specific data | - Using wood chips, and adding flue gas condenser (after economiser) increases efficiency by [%-point] | pct.-point |  | F, E | [1, 3] | ctrl | 2040 | 0.25
6.2 Boiler, biomass | Boiler, biomass | Technology-specific data | - Using wood chips, and adding flue gas condenser (after economiser) increases efficiency by [%-point] | pct.-point |  | F, E | [1, 3] | ctrl | 2050 | 0.25
6.2 Boiler, biomass | Boiler, biomass | Technology-specific data | - Using wood pellets, and adding flue gas condenser (after economiser) increases efficiency by [%-point] | pct.-point |  | E, I | [1, 3] | ctrl | 2025 | 0.12
6.2 Boiler, biomass | Boiler, biomass | Technology-specific data | - Using wood pellets, and adding flue gas condenser (after economiser) increases efficiency by [%-point] | pct.-point |  | E, I | [1, 3] | ctrl | 2030 | 0.12
6.2 Boiler, biomass | Boiler, biomass | Technology-specific data | - Using wood pellets, and adding flue gas condenser (after economiser) increases efficiency by [%-point] | pct.-point |  | E, I | [1, 3] | ctrl | 2035 | 0.12
6.2 Boiler, biomass | Boiler, biomass | Technology-specific data | - Using wood pellets, and adding flue gas condenser (after economiser) increases efficiency by [%-point] | pct.-point |  | E, I | [1, 3] | ctrl | 2040 | 0.12
6.2 Boiler, biomass | Boiler, biomass | Technology-specific data | - Using wood pellets, and adding flue gas condenser (after economiser) increases efficiency by [%-point] | pct.-point |  | E, I | [1, 3] | ctrl | 2050 | 0.12
6.2 Boiler, biomass | Boiler, biomass | Technology-specific data | - Wood pellets (instead of wood chips) reduces Variable O&M by [%] | pct. |  |  | 1 | ctrl | 2025 | 0.5
6.2 Boiler, biomass | Boiler, biomass | Technology-specific data | - Wood pellets (instead of wood chips) reduces Variable O&M by [%] | pct. |  |  | 1 | ctrl | 2030 | 0.5
6.2 Boiler, biomass | Boiler, biomass | Technology-specific data | - Wood pellets (instead of wood chips) reduces Variable O&M by [%] | pct. |  |  | 1 | ctrl | 2035 | 0.5
6.2 Boiler, biomass | Boiler, biomass | Technology-specific data | - Wood pellets (instead of wood chips) reduces Variable O&M by [%] | pct. |  |  | 1 | ctrl | 2040 | 0.5
6.2 Boiler, biomass | Boiler, biomass | Technology-specific data | - Wood pellets (instead of wood chips) reduces Variable O&M by [%] | pct. |  |  | 1 | ctrl | 2050 | 0.5
6.2 Boiler, biomass | Boiler, biomass | Technology-specific data | Indirect investment cost [M€/MW] | M€/MW |  | K, J |  | ctrl | 2025 | 0.23
6.2 Boiler, biomass | Boiler, biomass | Technology-specific data | Indirect investment cost [M€/MW] | M€/MW |  | K, J |  | ctrl | 2030 | 0.23
6.2 Boiler, biomass | Boiler, biomass | Technology-specific data | Indirect investment cost [M€/MW] | M€/MW |  | K, J |  | ctrl | 2035 | 0.23
6.2 Boiler, biomass | Boiler, biomass | Technology-specific data | Indirect investment cost [M€/MW] | M€/MW |  | K, J |  | ctrl | 2040 | 0.23
6.2 Boiler, biomass | Boiler, biomass | Technology-specific data | Indirect investment cost [M€/MW] | M€/MW |  | K, J |  | ctrl | 2050 | 0.23
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  | F | 1 | ctrl | 2025 | 0.02
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  | F | 1 | ctrl | 2030 | 0.02
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  | F | 1 | ctrl | 2035 | 0.02
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  | F | 1 | ctrl | 2040 | 0.02
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  | F | 1 | ctrl | 2050 | 0.02
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  | F | 1 | lower | 2025 | 0.02
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  | F | 1 | lower | 2050 | 0.02
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  | F | 1 | upper | 2025 | 0.02
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  | F | 1 | upper | 2050 | 0.02
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Construction time [years] | years |  | F | 1 | ctrl | 2025 | 1
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Construction time [years] | years |  | F | 1 | ctrl | 2030 | 1
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Construction time [years] | years |  | F | 1 | ctrl | 2035 | 1
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Construction time [years] | years |  | F | 1 | ctrl | 2040 | 1
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Construction time [years] | years |  | F | 1 | ctrl | 2050 | 1
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Construction time [years] | years |  | F | 1 | lower | 2025 | 0.5
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Construction time [years] | years |  | F | 1 | lower | 2050 | 0.5
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Construction time [years] | years |  | F | 1 | upper | 2025 | 1.5
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Construction time [years] | years |  | F | 1 | upper | 2050 | 1.5
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Forced outage [%] | pct. |  | F | 1 | ctrl | 2025 | 0.03
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Forced outage [%] | pct. |  | F | 1 | ctrl | 2030 | 0.03
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Forced outage [%] | pct. |  | F | 1 | ctrl | 2035 | 0.03
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Forced outage [%] | pct. |  | F | 1 | ctrl | 2040 | 0.03
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Forced outage [%] | pct. |  | F | 1 | ctrl | 2050 | 0.03
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Forced outage [%] | pct. |  | F | 1 | lower | 2025 | 0.03
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Forced outage [%] | pct. |  | F | 1 | lower | 2050 | 0.03
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Forced outage [%] | pct. |  | F | 1 | upper | 2025 | 0.03
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Forced outage [%] | pct. |  | F | 1 | upper | 2050 | 0.03
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | [3, 4] | ctrl | 2025 | 5
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | [3, 4] | ctrl | 2030 | 5
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | [3, 4] | ctrl | 2035 | 5
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | [3, 4] | ctrl | 2040 | 5
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | [3, 4] | ctrl | 2050 | 5
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | [3, 4] | lower | 2025 | 1.6
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | [3, 4] | lower | 2050 | 1.6
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | [3, 4] | upper | 2025 | 50
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | [3, 4] | upper | 2050 | 50
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | F | 1 | ctrl | 2025 | 2
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | F | 1 | ctrl | 2030 | 2
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | F | 1 | ctrl | 2035 | 2
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | F | 1 | ctrl | 2040 | 2
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | F | 1 | ctrl | 2050 | 2
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | F | 1 | lower | 2025 | 1.7
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | F | 1 | lower | 2050 | 1.5
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | F | 1 | upper | 2025 | 2.3
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | F | 1 | upper | 2050 | 2.5
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | F | 1 | ctrl | 2025 | 0.2
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | F | 1 | ctrl | 2030 | 0.2
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | F | 1 | ctrl | 2035 | 0.2
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | F | 1 | ctrl | 2040 | 0.2
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | F | 1 | ctrl | 2050 | 0.2
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | F | 1 | lower | 2025 | 0.14
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | F | 1 | lower | 2050 | 0.12
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | F | 1 | upper | 2025 | 0.25
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  | F | 1 | upper | 2050 | 0.27
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Technical lifetime [years] | years |  | E, F | 1 | ctrl | 2025 | 25
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Technical lifetime [years] | years |  | E, F | 1 | ctrl | 2030 | 25
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Technical lifetime [years] | years |  | E, F | 1 | ctrl | 2035 | 25
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Technical lifetime [years] | years |  | E, F | 1 | ctrl | 2040 | 25
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Technical lifetime [years] | years |  | E, F | 1 | ctrl | 2050 | 25
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Technical lifetime [years] | years |  | E, F | 1 | lower | 2025 | 20
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Technical lifetime [years] | years |  | E, F | 1 | lower | 2050 | 20
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Technical lifetime [years] | years |  | E, F | 1 | upper | 2025 | 35
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Technical lifetime [years] | years |  | E, F | 1 | upper | 2050 | 35
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A, B, C, D | 2 | ctrl | 2025 | 0.899
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A, B, C, D | 2 | ctrl | 2030 | 0.899
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A, B, C, D | 2 | ctrl | 2035 | 0.899
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A, B, C, D | 2 | ctrl | 2040 | 0.899
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A, B, C, D | 2 | ctrl | 2050 | 0.899
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A, B, C, D | 2 | lower | 2025 | 0.879
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A, B, C, D | 2 | lower | 2050 | 0.879
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A, B, C, D | 2 | upper | 2025 | 0.919
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A, B, C, D | 2 | upper | 2050 | 0.919
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A, B, C | 2 | ctrl | 2025 | 0.9
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A, B, C | 2 | ctrl | 2030 | 0.9
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A, B, C | 2 | ctrl | 2035 | 0.9
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A, B, C | 2 | ctrl | 2040 | 0.9
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A, B, C | 2 | ctrl | 2050 | 0.9
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A, B, C | 2 | lower | 2025 | 0.88
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A, B, C | 2 | lower | 2050 | 0.88
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A, B, C | 2 | upper | 2025 | 0.92
6.3 Boiler, coal | Boiler, coal | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A, B, C | 2 | upper | 2050 | 0.92
6.3 Boiler, coal | Boiler, coal | Financial data | - of which equipment [%] | pct. |  |  | 1 | ctrl | 2025 | 0.6
6.3 Boiler, coal | Boiler, coal | Financial data | - of which equipment [%] | pct. |  |  | 1 | ctrl | 2030 | 0.6
6.3 Boiler, coal | Boiler, coal | Financial data | - of which equipment [%] | pct. |  |  | 1 | ctrl | 2035 | 0.6
6.3 Boiler, coal | Boiler, coal | Financial data | - of which equipment [%] | pct. |  |  | 1 | ctrl | 2040 | 0.6
6.3 Boiler, coal | Boiler, coal | Financial data | - of which equipment [%] | pct. |  |  | 1 | ctrl | 2050 | 0.6
6.3 Boiler, coal | Boiler, coal | Financial data | - of which installation [%] | pct. |  |  | 1 | ctrl | 2025 | 0.4
6.3 Boiler, coal | Boiler, coal | Financial data | - of which installation [%] | pct. |  |  | 1 | ctrl | 2030 | 0.4
6.3 Boiler, coal | Boiler, coal | Financial data | - of which installation [%] | pct. |  |  | 1 | ctrl | 2035 | 0.4
6.3 Boiler, coal | Boiler, coal | Financial data | - of which installation [%] | pct. |  |  | 1 | ctrl | 2040 | 0.4
6.3 Boiler, coal | Boiler, coal | Financial data | - of which installation [%] | pct. |  |  | 1 | ctrl | 2050 | 0.4
6.3 Boiler, coal | Boiler, coal | Financial data | Fixed O&M [EUR/MW_y] | EUR/MW_y | 2025 | E, F | 1 | ctrl | 2025 | 40000
6.3 Boiler, coal | Boiler, coal | Financial data | Fixed O&M [EUR/MW_y] | EUR/MW_y | 2025 | E, F | 1 | ctrl | 2030 | 39500
6.3 Boiler, coal | Boiler, coal | Financial data | Fixed O&M [EUR/MW_y] | EUR/MW_y | 2025 | E, F | 1 | ctrl | 2035 | 39000
6.3 Boiler, coal | Boiler, coal | Financial data | Fixed O&M [EUR/MW_y] | EUR/MW_y | 2025 | E, F | 1 | ctrl | 2040 | 38500
6.3 Boiler, coal | Boiler, coal | Financial data | Fixed O&M [EUR/MW_y] | EUR/MW_y | 2025 | E, F | 1 | ctrl | 2050 | 37500
6.3 Boiler, coal | Boiler, coal | Financial data | Nominal investment (*total) [MEUR/MW] | MEUR/MW | 2025 | F, H | 1 | ctrl | 2025 | 0.565
6.3 Boiler, coal | Boiler, coal | Financial data | Nominal investment (*total) [MEUR/MW] | MEUR/MW | 2025 | F, H | 1 | ctrl | 2030 | 0.545
6.3 Boiler, coal | Boiler, coal | Financial data | Nominal investment (*total) [MEUR/MW] | MEUR/MW | 2025 | F, H | 1 | ctrl | 2035 | 0.533
6.3 Boiler, coal | Boiler, coal | Financial data | Nominal investment (*total) [MEUR/MW] | MEUR/MW | 2025 | F, H | 1 | ctrl | 2040 | 0.521
6.3 Boiler, coal | Boiler, coal | Financial data | Nominal investment (*total) [MEUR/MW] | MEUR/MW | 2025 | F, H | 1 | ctrl | 2050 | 0.515
6.3 Boiler, coal | Boiler, coal | Financial data | Variable O&M [EUR/MWh] | EUR/MWh | 2025 | F | 1 | ctrl | 2025 | 1.45
6.3 Boiler, coal | Boiler, coal | Financial data | Variable O&M [EUR/MWh] | EUR/MWh | 2025 | F | 1 | ctrl | 2030 | 1.45
6.3 Boiler, coal | Boiler, coal | Financial data | Variable O&M [EUR/MWh] | EUR/MWh | 2025 | F | 1 | ctrl | 2035 | 1.45
6.3 Boiler, coal | Boiler, coal | Financial data | Variable O&M [EUR/MWh] | EUR/MWh | 2025 | F | 1 | ctrl | 2040 | 1.45
6.3 Boiler, coal | Boiler, coal | Financial data | Variable O&M [EUR/MWh] | EUR/MWh | 2025 | F | 1 | ctrl | 2050 | 1.45
6.3 Boiler, coal | Boiler, coal | Regulation ability | Cold start-up time [hours] | hours |  | F | 1 | ctrl | 2025 | 0.5
6.3 Boiler, coal | Boiler, coal | Regulation ability | Cold start-up time [hours] | hours |  | F | 1 | ctrl | 2030 | 0.5
6.3 Boiler, coal | Boiler, coal | Regulation ability | Cold start-up time [hours] | hours |  | F | 1 | ctrl | 2035 | 0.5
6.3 Boiler, coal | Boiler, coal | Regulation ability | Cold start-up time [hours] | hours |  | F | 1 | ctrl | 2040 | 0.5
6.3 Boiler, coal | Boiler, coal | Regulation ability | Cold start-up time [hours] | hours |  | F | 1 | ctrl | 2050 | 0.5
6.3 Boiler, coal | Boiler, coal | Regulation ability | Minimum load (of full load) [%] | pct. |  | E | 1 | ctrl | 2025 | 0.15
6.3 Boiler, coal | Boiler, coal | Regulation ability | Minimum load (of full load) [%] | pct. |  | E | 1 | ctrl | 2030 | 0.15
6.3 Boiler, coal | Boiler, coal | Regulation ability | Minimum load (of full load) [%] | pct. |  | E | 1 | ctrl | 2035 | 0.15
6.3 Boiler, coal | Boiler, coal | Regulation ability | Minimum load (of full load) [%] | pct. |  | E | 1 | ctrl | 2040 | 0.15
6.3 Boiler, coal | Boiler, coal | Regulation ability | Minimum load (of full load) [%] | pct. |  | E | 1 | ctrl | 2050 | 0.15
6.3 Boiler, coal | Boiler, coal | Regulation ability | Secondary regulation (of full load, per minute) [%] | pct. |  | F | 1 | ctrl | 2025 | 0.1
6.3 Boiler, coal | Boiler, coal | Regulation ability | Secondary regulation (of full load, per minute) [%] | pct. |  | F | 1 | ctrl | 2030 | 0.1
6.3 Boiler, coal | Boiler, coal | Regulation ability | Secondary regulation (of full load, per minute) [%] | pct. |  | F | 1 | ctrl | 2035 | 0.1
6.3 Boiler, coal | Boiler, coal | Regulation ability | Secondary regulation (of full load, per minute) [%] | pct. |  | F | 1 | ctrl | 2040 | 0.1
6.3 Boiler, coal | Boiler, coal | Regulation ability | Secondary regulation (of full load, per minute) [%] | pct. |  | F | 1 | ctrl | 2050 | 0.1
6.3 Boiler, coal | Boiler, coal | Regulation ability | Warm start-up time [hours] | hours |  | F | 1 | ctrl | 2025 | 0.25
6.3 Boiler, coal | Boiler, coal | Regulation ability | Warm start-up time [hours] | hours |  | F | 1 | ctrl | 2030 | 0.25
6.3 Boiler, coal | Boiler, coal | Regulation ability | Warm start-up time [hours] | hours |  | F | 1 | ctrl | 2035 | 0.25
6.3 Boiler, coal | Boiler, coal | Regulation ability | Warm start-up time [hours] | hours |  | F | 1 | ctrl | 2040 | 0.25
6.3 Boiler, coal | Boiler, coal | Regulation ability | Warm start-up time [hours] | hours |  | F | 1 | ctrl | 2050 | 0.25
6.3 Boiler, coal | Boiler, coal | Technology-specific data | - Hot water boiler instead of steam boiler increases efficiency by [%-point] | pct.-point |  | G |  | ctrl | 2025 | 0.01
6.3 Boiler, coal | Boiler, coal | Technology-specific data | - Hot water boiler instead of steam boiler increases efficiency by [%-point] | pct.-point |  | G |  | ctrl | 2030 | 0.01
6.3 Boiler, coal | Boiler, coal | Technology-specific data | - Hot water boiler instead of steam boiler increases efficiency by [%-point] | pct.-point |  | G |  | ctrl | 2035 | 0.01
6.3 Boiler, coal | Boiler, coal | Technology-specific data | - Hot water boiler instead of steam boiler increases efficiency by [%-point] | pct.-point |  | G |  | ctrl | 2040 | 0.01
6.3 Boiler, coal | Boiler, coal | Technology-specific data | - Hot water boiler instead of steam boiler increases efficiency by [%-point] | pct.-point |  | G |  | ctrl | 2050 | 0.01
6.3 Boiler, coal | Boiler, coal | Technology-specific data | Indirect investment cost [M€/MW] | M€/MW |  | I, J |  | ctrl | 2025 | 0.23
6.3 Boiler, coal | Boiler, coal | Technology-specific data | Indirect investment cost [M€/MW] | M€/MW |  | I, J |  | ctrl | 2030 | 0.23
6.3 Boiler, coal | Boiler, coal | Technology-specific data | Indirect investment cost [M€/MW] | M€/MW |  | I, J |  | ctrl | 2035 | 0.23
6.3 Boiler, coal | Boiler, coal | Technology-specific data | Indirect investment cost [M€/MW] | M€/MW |  | I, J |  | ctrl | 2040 | 0.23
6.3 Boiler, coal | Boiler, coal | Technology-specific data | Indirect investment cost [M€/MW] | M€/MW |  | I, J |  | ctrl | 2050 | 0.23
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [8, 9] | ctrl | 2025 | 0.0025
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [8, 9] | ctrl | 2030 | 0.0025
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [8, 9] | ctrl | 2035 | 0.0025
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [8, 9] | ctrl | 2040 | 0.0025
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [8, 9] | ctrl | 2050 | 0.0025
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [8, 9] | lower | 2025 | 0.001
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [8, 9] | lower | 2050 | 0.001
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [8, 9] | upper | 2025 | 0.01
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  |  | [8, 9] | upper | 2050 | 0.01
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Construction time [years] | years |  |  | 2 | ctrl | 2025 | 0.01
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Construction time [years] | years |  |  | 2 | ctrl | 2030 | 0.01
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Construction time [years] | years |  |  | 2 | ctrl | 2035 | 0.01
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Construction time [years] | years |  |  | 2 | ctrl | 2040 | 0.01
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Construction time [years] | years |  |  | 2 | ctrl | 2050 | 0.01
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Construction time [years] | years |  |  | 2 | lower | 2025 | 0.01
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Construction time [years] | years |  |  | 2 | lower | 2050 | 0.01
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Construction time [years] | years |  |  | 2 | upper | 2025 | 0.04
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Construction time [years] | years |  |  | 2 | upper | 2050 | 0.04
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Forced outage [%] | pct. |  |  | 2 | ctrl | 2025 | 0.0025
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Forced outage [%] | pct. |  |  | 2 | ctrl | 2030 | 0.0025
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Forced outage [%] | pct. |  |  | 2 | ctrl | 2035 | 0.0025
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Forced outage [%] | pct. |  |  | 2 | ctrl | 2040 | 0.0025
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Forced outage [%] | pct. |  |  | 2 | ctrl | 2050 | 0.0025
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Forced outage [%] | pct. |  |  | 2 | lower | 2025 | 0
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Forced outage [%] | pct. |  |  | 2 | lower | 2050 | 0
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Forced outage [%] | pct. |  |  | 2 | upper | 2025 | 0.005
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Forced outage [%] | pct. |  |  | 2 | upper | 2050 | 0.005
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | 2 | ctrl | 2025 | 2.5
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | 2 | ctrl | 2030 | 2.5
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | 2 | ctrl | 2035 | 2.5
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | 2 | ctrl | 2040 | 2.5
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | 2 | ctrl | 2050 | 2.5
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | 2 | lower | 2025 | 1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | 2 | lower | 2050 | 1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | 2 | upper | 2025 | 10
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | 2 | upper | 2050 | 10
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | ctrl | 2025 | 0.5
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | ctrl | 2030 | 0.5
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | ctrl | 2035 | 0.5
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | ctrl | 2040 | 0.5
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | ctrl | 2050 | 0.5
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | lower | 2025 | 0
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | lower | 2050 | 0
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | upper | 2025 | 1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 2 | upper | 2050 | 1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Technical lifetime [years] | years |  |  | 4 | ctrl | 2025 | 15
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Technical lifetime [years] | years |  |  | 4 | ctrl | 2030 | 15
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Technical lifetime [years] | years |  |  | 4 | ctrl | 2035 | 15
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Technical lifetime [years] | years |  |  | 4 | ctrl | 2040 | 15
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Technical lifetime [years] | years |  |  | 4 | ctrl | 2050 | 15
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Technical lifetime [years] | years |  |  | 4 | lower | 2025 | 10
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Technical lifetime [years] | years |  |  | 4 | lower | 2050 | 10
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Technical lifetime [years] | years |  |  | 4 | upper | 2025 | 20
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Technical lifetime [years] | years |  |  | 4 | upper | 2050 | 20
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A | 2 | ctrl | 2025 | 1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A | 2 | ctrl | 2030 | 1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A | 2 | ctrl | 2035 | 1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A | 2 | ctrl | 2040 | 1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A | 2 | ctrl | 2050 | 1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A | 2 | lower | 2025 | 1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A | 2 | lower | 2050 | 1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A | 2 | upper | 2025 | 1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A | 2 | upper | 2050 | 1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A | 2 | ctrl | 2025 | 1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A | 2 | ctrl | 2030 | 1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A | 2 | ctrl | 2035 | 1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A | 2 | ctrl | 2040 | 1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A | 2 | ctrl | 2050 | 1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A | 2 | lower | 2025 | 1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A | 2 | lower | 2050 | 1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A | 2 | upper | 2025 | 1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A | 2 | upper | 2050 | 1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Environment | CH4 [g per GJ fuel] | g/GJfuel |  |  | 1 | ctrl | 2025 | 3
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Environment | CH4 [g per GJ fuel] | g/GJfuel |  |  | 1 | ctrl | 2030 | 2
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Environment | CH4 [g per GJ fuel] | g/GJfuel |  |  | 1 | ctrl | 2035 | 2
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Environment | CH4 [g per GJ fuel] | g/GJfuel |  |  | 1 | ctrl | 2040 | 2
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Environment | CH4 [g per GJ fuel] | g/GJfuel |  |  | 1 | ctrl | 2050 | 2
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Environment | N2O [g per GJ fuel] | g/GJfuel |  |  | 1 | ctrl | 2025 | 1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Environment | N2O [g per GJ fuel] | g/GJfuel |  |  | 1 | ctrl | 2030 | 1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Environment | N2O [g per GJ fuel] | g/GJfuel |  |  | 1 | ctrl | 2035 | 1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Environment | N2O [g per GJ fuel] | g/GJfuel |  |  | 1 | ctrl | 2040 | 1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Environment | N2O [g per GJ fuel] | g/GJfuel |  |  | 1 | ctrl | 2050 | 1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Environment | NOX [g per GJ fuel] | g/GJfuel |  |  | 1 | ctrl | 2025 | 9
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Environment | NOX [g per GJ fuel] | g/GJfuel |  |  | 1 | ctrl | 2030 | 7
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Environment | NOX [g per GJ fuel] | g/GJfuel |  |  | 1 | ctrl | 2035 | 7
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Environment | NOX [g per GJ fuel] | g/GJfuel |  |  | 1 | ctrl | 2040 | 6
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Environment | NOX [g per GJ fuel] | g/GJfuel |  |  | 1 | ctrl | 2050 | 6
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Environment | PM2.5 [g per GJ fuel] | g/GJfuel |  |  | 1 | ctrl | 2025 | 0.1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Environment | PM2.5 [g per GJ fuel] | g/GJfuel |  |  | 1 | ctrl | 2030 | 0.1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Environment | PM2.5 [g per GJ fuel] | g/GJfuel |  |  | 1 | ctrl | 2035 | 0.1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Environment | PM2.5 [g per GJ fuel] | g/GJfuel |  |  | 1 | ctrl | 2040 | 0.1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Environment | PM2.5 [g per GJ fuel] | g/GJfuel |  |  | 1 | ctrl | 2050 | 0.1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Environment | SO2 [g per GJ fuel] | g/GJfuel |  |  | 1 | ctrl | 2025 | 0.3
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Environment | SO2 [g per GJ fuel] | g/GJfuel |  |  | 1 | ctrl | 2030 | 0.3
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Environment | SO2 [g per GJ fuel] | g/GJfuel |  |  | 1 | ctrl | 2035 | 0.3
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Environment | SO2 [g per GJ fuel] | g/GJfuel |  |  | 1 | ctrl | 2040 | 0.3
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Environment | SO2 [g per GJ fuel] | g/GJfuel |  |  | 1 | ctrl | 2050 | 0.3
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Financial data | - of which equipment [%] | pct. |  |  | 7 | ctrl | 2025 | 0.66667
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Financial data | - of which equipment [%] | pct. |  |  | 7 | ctrl | 2030 | 0.66667
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Financial data | - of which equipment [%] | pct. |  |  | 7 | ctrl | 2035 | 0.66667
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Financial data | - of which equipment [%] | pct. |  |  | 7 | ctrl | 2040 | 0.66667
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Financial data | - of which equipment [%] | pct. |  |  | 7 | ctrl | 2050 | 0.66667
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Financial data | - of which installation [%] | pct. |  |  | 7 | ctrl | 2025 | 0.33333
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Financial data | - of which installation [%] | pct. |  |  | 7 | ctrl | 2030 | 0.33333
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Financial data | - of which installation [%] | pct. |  |  | 7 | ctrl | 2035 | 0.33333
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Financial data | - of which installation [%] | pct. |  |  | 7 | ctrl | 2040 | 0.33333
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Financial data | - of which installation [%] | pct. |  |  | 7 | ctrl | 2050 | 0.33333
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  | C | [2, 1] | ctrl | 2025 | 213
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  | C | [2, 1] | ctrl | 2030 | 208
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  | C | [2, 1] | ctrl | 2035 | 205
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  | C | [2, 1] | ctrl | 2040 | 202
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  | C | [2, 1] | ctrl | 2050 | 181
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Financial data | Nominal investment [M€/MW] | M€/MW |  | B | [4, 7] | ctrl | 2025 | 0.0176
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Financial data | Nominal investment [M€/MW] | M€/MW |  | B | [4, 7] | ctrl | 2030 | 0.0176
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Financial data | Nominal investment [M€/MW] | M€/MW |  | B | [4, 7] | ctrl | 2035 | 0.0176
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Financial data | Nominal investment [M€/MW] | M€/MW |  | B | [4, 7] | ctrl | 2040 | 0.0176
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Financial data | Nominal investment [M€/MW] | M€/MW |  | B | [4, 7] | ctrl | 2050 | 0.0176
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Financial data | Variable O&M [€/MWh] | €/MWh |  | C | 1 | ctrl | 2025 | 0.117
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Financial data | Variable O&M [€/MWh] | €/MWh |  | C | 1 | ctrl | 2030 | 0.105
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Financial data | Variable O&M [€/MWh] | €/MWh |  | C | 1 | ctrl | 2035 | 0.105
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Financial data | Variable O&M [€/MWh] | €/MWh |  | C | 1 | ctrl | 2040 | 0.105
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Financial data | Variable O&M [€/MWh] | €/MWh |  | C | 1 | ctrl | 2050 | 0.105
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Regulation Ability | Cold start-up time [hours] | hours |  |  | 2 | ctrl | 2025 | 0.01
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Regulation Ability | Cold start-up time [hours] | hours |  |  | 2 | ctrl | 2030 | 0.01
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Regulation Ability | Cold start-up time [hours] | hours |  |  | 2 | ctrl | 2035 | 0.01
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Regulation Ability | Cold start-up time [hours] | hours |  |  | 2 | ctrl | 2040 | 0.01
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Regulation Ability | Cold start-up time [hours] | hours |  |  | 2 | ctrl | 2050 | 0.01
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 6 | ctrl | 2025 | 0.1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 6 | ctrl | 2030 | 0.1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 6 | ctrl | 2035 | 0.1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 6 | ctrl | 2040 | 0.1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 6 | ctrl | 2050 | 0.1
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Regulation Ability | Warm start-up time [hours] | hours |  |  | 2 | ctrl | 2025 | 0.01
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Regulation Ability | Warm start-up time [hours] | hours |  |  | 2 | ctrl | 2030 | 0.01
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Regulation Ability | Warm start-up time [hours] | hours |  |  | 2 | ctrl | 2035 | 0.01
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Regulation Ability | Warm start-up time [hours] | hours |  |  | 2 | ctrl | 2040 | 0.01
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Regulation Ability | Warm start-up time [hours] | hours |  |  | 2 | ctrl | 2050 | 0.01
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Technology-specific data | Indirect investments cost [M€/MW] | M€/MW |  | E | - | ctrl | 2025 | -
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Technology-specific data | Indirect investments cost [M€/MW] | M€/MW |  | E | - | ctrl | 2030 | -
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Technology-specific data | Indirect investments cost [M€/MW] | M€/MW |  | E | - | ctrl | 2035 | -
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Technology-specific data | Indirect investments cost [M€/MW] | M€/MW |  | E | - | ctrl | 2040 | -
7.1 Direct firing Natural Gas | Direct firing, Natural gas | Technology-specific data | Indirect investments cost [M€/MW] | M€/MW |  | E | - | ctrl | 2050 | -
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  | B | [8, 9] | ctrl | 2025 | 0.0025
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  | B | [8, 9] | ctrl | 2030 | 0.0025
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  | B | [8, 9] | ctrl | 2035 | 0.0025
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  | B | [8, 9] | ctrl | 2040 | 0.0025
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  | B | [8, 9] | ctrl | 2050 | 0.0025
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  | B | [8, 9] | lower | 2025 | 0.001
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  | B | [8, 9] | lower | 2050 | 0.001
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  | B | [8, 9] | upper | 2025 | 0.01
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  | B | [8, 9] | upper | 2050 | 0.01
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Construction time [years] | years |  | I | [2, 4] | ctrl | 2025 | 0.01
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Construction time [years] | years |  | I | [2, 4] | ctrl | 2030 | 0.01
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Construction time [years] | years |  | I | [2, 4] | ctrl | 2035 | 0.01
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Construction time [years] | years |  | I | [2, 4] | ctrl | 2040 | 0.01
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Construction time [years] | years |  | I | [2, 4] | ctrl | 2050 | 0.01
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Construction time [years] | years |  | I | [2, 4] | lower | 2025 | 0.001
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Construction time [years] | years |  | I | [2, 4] | lower | 2050 | 0.001
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Construction time [years] | years |  | I | [2, 4] | upper | 2025 | 0.015
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Construction time [years] | years |  | I | [2, 4] | upper | 2050 | 0.015
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Forced outage [%] | pct. |  |  | 2 | ctrl | 2025 | 0.0025
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Forced outage [%] | pct. |  |  | 2 | ctrl | 2030 | 0.0025
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Forced outage [%] | pct. |  |  | 2 | ctrl | 2035 | 0.0025
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Forced outage [%] | pct. |  |  | 2 | ctrl | 2040 | 0.0025
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Forced outage [%] | pct. |  |  | 2 | ctrl | 2050 | 0.0025
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Forced outage [%] | pct. |  |  | 2 | lower | 2025 | 0
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Forced outage [%] | pct. |  |  | 2 | lower | 2050 | 0
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Forced outage [%] | pct. |  |  | 2 | upper | 2025 | 0.005
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Forced outage [%] | pct. |  |  | 2 | upper | 2050 | 0.005
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  |  | ctrl | 2025 | 10
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  |  | ctrl | 2030 | 10
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  |  | ctrl | 2035 | 10
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  |  | ctrl | 2040 | 10
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  |  | ctrl | 2050 | 10
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  |  | lower | 2025 | 10
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  |  | lower | 2050 | 10
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  |  | upper | 2025 | 10
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  |  | upper | 2050 | 10
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 4 | ctrl | 2025 | 3.5
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 4 | ctrl | 2030 | 3.5
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 4 | ctrl | 2035 | 3.5
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 4 | ctrl | 2040 | 3.5
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 4 | ctrl | 2050 | 3.5
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 4 | lower | 2025 | 2
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 4 | lower | 2050 | 2
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 4 | upper | 2025 | 5
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Planned outage [weeks per year] | weeks/year |  |  | 4 | upper | 2050 | 5
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Technical lifetime [years] | years |  |  | [2, 4] | ctrl | 2025 | 15
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Technical lifetime [years] | years |  |  | [2, 4] | ctrl | 2030 | 15
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Technical lifetime [years] | years |  |  | [2, 4] | ctrl | 2035 | 15
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Technical lifetime [years] | years |  |  | [2, 4] | ctrl | 2040 | 15
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Technical lifetime [years] | years |  |  | [2, 4] | ctrl | 2050 | 15
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Technical lifetime [years] | years |  |  | [2, 4] | lower | 2025 | 10
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Technical lifetime [years] | years |  |  | [2, 4] | lower | 2050 | 10
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Technical lifetime [years] | years |  |  | [2, 4] | upper | 2025 | 20
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Technical lifetime [years] | years |  |  | [2, 4] | upper | 2050 | 20
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A | 2 | ctrl | 2025 | 1
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A | 2 | ctrl | 2030 | 1
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A | 2 | ctrl | 2035 | 1
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A | 2 | ctrl | 2040 | 1
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A | 2 | ctrl | 2050 | 1
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A | 2 | lower | 2025 | 1
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A | 2 | lower | 2050 | 1
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A | 2 | upper | 2025 | 1
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A | 2 | upper | 2050 | 1
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A | 2 | ctrl | 2025 | 1
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A | 2 | ctrl | 2030 | 1
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A | 2 | ctrl | 2035 | 1
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A | 2 | ctrl | 2040 | 1
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A | 2 | ctrl | 2050 | 1
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A | 2 | lower | 2025 | 1
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A | 2 | lower | 2050 | 1
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A | 2 | upper | 2025 | 1
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A | 2 | upper | 2050 | 1
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Financial data | - of which equipment [%] | pct. |  |  | 7 | ctrl | 2025 | 0.66667
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Financial data | - of which equipment [%] | pct. |  |  | 7 | ctrl | 2030 | 0.66667
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Financial data | - of which equipment [%] | pct. |  |  | 7 | ctrl | 2035 | 0.66667
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Financial data | - of which equipment [%] | pct. |  |  | 7 | ctrl | 2040 | 0.66667
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Financial data | - of which equipment [%] | pct. |  |  | 7 | ctrl | 2050 | 0.66667
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Financial data | - of which installation [%] | pct. |  |  | 7 | ctrl | 2025 | 0.33333
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Financial data | - of which installation [%] | pct. |  |  | 7 | ctrl | 2030 | 0.33333
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Financial data | - of which installation [%] | pct. |  |  | 7 | ctrl | 2035 | 0.33333
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Financial data | - of which installation [%] | pct. |  |  | 7 | ctrl | 2040 | 0.33333
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Financial data | - of which installation [%] | pct. |  |  | 7 | ctrl | 2050 | 0.33333
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  | C | [2, 1] | ctrl | 2025 | 3986
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  | C | [2, 1] | ctrl | 2030 | 3869
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  | C | [2, 1] | ctrl | 2035 | 3810
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  | C | [2, 1] | ctrl | 2040 | 3751
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Financial data | Fixed O&M [€/MJ/s/year] | €/MJ/s/year |  | C | [2, 1] | ctrl | 2050 | 3634
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Financial data | Nominal investment [M€/MW] | M€/MW |  | E, G, H | [4, 7] | ctrl | 2025 | 0.258
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Financial data | Nominal investment [M€/MW] | M€/MW |  | E, G, H | [4, 7] | ctrl | 2030 | 0.258
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Financial data | Nominal investment [M€/MW] | M€/MW |  | E, G, H | [4, 7] | ctrl | 2035 | 0.258
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Financial data | Nominal investment [M€/MW] | M€/MW |  | E, G, H | [4, 7] | ctrl | 2040 | 0.258
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Financial data | Nominal investment [M€/MW] | M€/MW |  | E, G, H | [4, 7] | ctrl | 2050 | 0.258
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Financial data | Variable O&M [€/MWh] | €/MWh |  | C | [2, 7] | ctrl | 2025 | 0.167
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Financial data | Variable O&M [€/MWh] | €/MWh |  | C | [2, 7] | ctrl | 2030 | 0.167
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Financial data | Variable O&M [€/MWh] | €/MWh |  | C | [2, 7] | ctrl | 2035 | 0.167
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Financial data | Variable O&M [€/MWh] | €/MWh |  | C | [2, 7] | ctrl | 2040 | 0.167
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Financial data | Variable O&M [€/MWh] | €/MWh |  | C | [2, 7] | ctrl | 2050 | 0.167
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Regulation Ability | Cold start-up time [hours] | hours |  | F | 2 | ctrl | 2025 | 0.01
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Regulation Ability | Cold start-up time [hours] | hours |  | F | 2 | ctrl | 2030 | 0.01
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Regulation Ability | Cold start-up time [hours] | hours |  | F | 2 | ctrl | 2035 | 0.01
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Regulation Ability | Cold start-up time [hours] | hours |  | F | 2 | ctrl | 2040 | 0.01
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Regulation Ability | Cold start-up time [hours] | hours |  | F | 2 | ctrl | 2050 | 0.01
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 6 | ctrl | 2025 | 0.1
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 6 | ctrl | 2030 | 0.1
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 6 | ctrl | 2035 | 0.1
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 6 | ctrl | 2040 | 0.1
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Regulation Ability | Minimum load [% of full load] | pct.offullload |  |  | 6 | ctrl | 2050 | 0.1
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Regulation Ability | Warm start-up time [hours] | hours |  | F | 2 | ctrl | 2025 | 0.01
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Regulation Ability | Warm start-up time [hours] | hours |  | F | 2 | ctrl | 2030 | 0.01
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Regulation Ability | Warm start-up time [hours] | hours |  | F | 2 | ctrl | 2035 | 0.01
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Regulation Ability | Warm start-up time [hours] | hours |  | F | 2 | ctrl | 2040 | 0.01
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Regulation Ability | Warm start-up time [hours] | hours |  | F | 2 | ctrl | 2050 | 0.01
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Technology-specific data | Indirect investments cost [M€/MW] | M€/MW |  | J |  | ctrl | 2025 | -
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Technology-specific data | Indirect investments cost [M€/MW] | M€/MW |  | J |  | ctrl | 2030 | -
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Technology-specific data | Indirect investments cost [M€/MW] | M€/MW |  | J |  | ctrl | 2035 | -
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Technology-specific data | Indirect investments cost [M€/MW] | M€/MW |  | J |  | ctrl | 2040 | -
7.2 Direct firing Solid Fuels | Direct firing, Solid fuels | Technology-specific data | Indirect investments cost [M€/MW] | M€/MW |  | J |  | ctrl | 2050 | -
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  | B | [6, 7] | ctrl | 2025 | 0.0025
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  | B | [6, 7] | ctrl | 2030 | 0.0025
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  | B | [6, 7] | ctrl | 2035 | 0.0025
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  | B | [6, 7] | ctrl | 2040 | 0.0025
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  | B | [6, 7] | ctrl | 2050 | 0.0025
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  | B | [6, 7] | lower | 2025 | 0.001
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  | B | [6, 7] | lower | 2050 | 0.001
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  | B | [6, 7] | upper | 2025 | 0.01
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Auxiliary electricity consumption [% of heat gen] | pct.ofheatgen |  | B | [6, 7] | upper | 2050 | 0.01
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2025 | 0.04
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2030 | 0.04
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2035 | 0.04
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2040 | 0.04
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Construction time [years] | years |  |  | 1 | ctrl | 2050 | 0.04
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Forced outage [days] | days |  | C | 1 | ctrl | 2025 | 0
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Forced outage [days] | days |  | C | 1 | ctrl | 2030 | 0
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Forced outage [days] | days |  | C | 1 | ctrl | 2035 | 0
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Forced outage [days] | days |  | C | 1 | ctrl | 2040 | 0
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Forced outage [days] | days |  | C | 1 | ctrl | 2050 | 0
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Forced outage [days] | days |  | C | 1 | lower | 2025 | 0
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Forced outage [days] | days |  | C | 1 | lower | 2050 | 0
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Forced outage [days] | days |  | C | 1 | upper | 2025 | 0.5
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Forced outage [days] | days |  | C | 1 | upper | 2050 | 0.5
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | [1, 2] | ctrl | 2025 | 5
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | [1, 2] | ctrl | 2030 | 5
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | [1, 2] | ctrl | 2035 | 5
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | [1, 2] | ctrl | 2040 | 5
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | [1, 2] | ctrl | 2050 | 5
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | [1, 2] | lower | 2025 | 1
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | [1, 2] | lower | 2050 | 1
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | [1, 2] | upper | 2025 | 10
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Heat generation capacity for one unit [MW] | MW |  |  | [1, 2] | upper | 2050 | 10
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | C | 1 | ctrl | 2025 | 0
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | C | 1 | ctrl | 2030 | 0
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | C | 1 | ctrl | 2035 | 0
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | C | 1 | ctrl | 2040 | 0
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | C | 1 | ctrl | 2050 | 0
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | C | 1 | lower | 2025 | 0
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | C | 1 | lower | 2050 | 0
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | C | 1 | upper | 2025 | 1
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Planned outage [weeks per year] | weeks/year |  | C | 1 | upper | 2050 | 1
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 5 | ctrl | 2025 | 0.0125
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 5 | ctrl | 2030 | 0.005
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 5 | ctrl | 2035 | 0.001
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 5 | ctrl | 2040 | 0.001
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Space requirement [1000 m2/MW_e] | 1000m2/MW_e |  |  | 5 | ctrl | 2050 | 0.001
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Technical lifetime [years] | years |  |  | 8 | ctrl | 2025 | 20
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Technical lifetime [years] | years |  |  | 8 | ctrl | 2030 | 20
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Technical lifetime [years] | years |  |  | 8 | ctrl | 2035 | 20
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Technical lifetime [years] | years |  |  | 8 | ctrl | 2040 | 20
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Technical lifetime [years] | years |  |  | 8 | ctrl | 2050 | 20
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A | [3, 4] | ctrl | 2025 | 1
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A | [3, 4] | ctrl | 2030 | 1
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A | [3, 4] | ctrl | 2035 | 1
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A | [3, 4] | ctrl | 2040 | 1
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A | [3, 4] | ctrl | 2050 | 1
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A | [3, 4] | lower | 2025 | 1
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A | [3, 4] | lower | 2050 | 1
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A | [3, 4] | upper | 2025 | 1
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Total efficiency, net [%], annual average | pct. |  | A | [3, 4] | upper | 2050 | 1
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A | [3, 4] | ctrl | 2025 | 1
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A | [3, 4] | ctrl | 2030 | 1
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A | [3, 4] | ctrl | 2035 | 1
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A | [3, 4] | ctrl | 2040 | 1
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A | [3, 4] | ctrl | 2050 | 1
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A | [3, 4] | lower | 2025 | 1
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A | [3, 4] | lower | 2050 | 1
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A | [3, 4] | upper | 2025 | 1
7.3 Direct electric firing | Direct electric heating | Energy/technical data | Total efficiency, net [%], nominel load | pct. |  | A | [3, 4] | upper | 2050 | 1
7.3 Direct electric firing | Direct electric heating | Financial data | - of which equipment [%] | pct. |  |  | 9 | ctrl | 2025 | 0.66667
7.3 Direct electric firing | Direct electric heating | Financial data | - of which equipment [%] | pct. |  |  | 9 | ctrl | 2030 | 0.66667
7.3 Direct electric firing | Direct electric heating | Financial data | - of which equipment [%] | pct. |  |  | 9 | ctrl | 2035 | 0.66667
7.3 Direct electric firing | Direct electric heating | Financial data | - of which equipment [%] | pct. |  |  | 9 | ctrl | 2040 | 0.66667
7.3 Direct electric firing | Direct electric heating | Financial data | - of which equipment [%] | pct. |  |  | 9 | ctrl | 2050 | 0.66667
7.3 Direct electric firing | Direct electric heating | Financial data | - of which installation [%] | pct. |  |  | 9 | ctrl | 2025 | 0.33333
7.3 Direct electric firing | Direct electric heating | Financial data | - of which installation [%] | pct. |  |  | 9 | ctrl | 2030 | 0.33333
7.3 Direct electric firing | Direct electric heating | Financial data | - of which installation [%] | pct. |  |  | 9 | ctrl | 2035 | 0.33333
7.3 Direct electric firing | Direct electric heating | Financial data | - of which installation [%] | pct. |  |  | 9 | ctrl | 2040 | 0.33333
7.3 Direct electric firing | Direct electric heating | Financial data | - of which installation [%] | pct. |  |  | 9 | ctrl | 2050 | 0.33333
7.3 Direct electric firing | Direct electric heating | Financial data | Fixed O&M [EUR/MW_y] | EUR/MW_y | 2025 | C | 5 | ctrl | 2025 | 0
7.3 Direct electric firing | Direct electric heating | Financial data | Fixed O&M [EUR/MW_y] | EUR/MW_y | 2025 | C | 5 | ctrl | 2030 | 0
7.3 Direct electric firing | Direct electric heating | Financial data | Fixed O&M [EUR/MW_y] | EUR/MW_y | 2025 | C | 5 | ctrl | 2035 | 0
7.3 Direct electric firing | Direct electric heating | Financial data | Fixed O&M [EUR/MW_y] | EUR/MW_y | 2025 | C | 5 | ctrl | 2040 | 0
7.3 Direct electric firing | Direct electric heating | Financial data | Fixed O&M [EUR/MW_y] | EUR/MW_y | 2025 | C | 5 | ctrl | 2050 | 0
7.3 Direct electric firing | Direct electric heating | Financial data | Nominal investment (*total) [MEUR/MW] , from last update in 2019 | MEUR/MW | 2025 | E, H | [9, 10] | ctrl | 2025 | 0.07
7.3 Direct electric firing | Direct electric heating | Financial data | Nominal investment (*total) [MEUR/MW] , from last update in 2019 | MEUR/MW | 2025 | E, H | [9, 10] | ctrl | 2030 | 0.07
7.3 Direct electric firing | Direct electric heating | Financial data | Nominal investment (*total) [MEUR/MW] , from last update in 2019 | MEUR/MW | 2025 | E, H | [9, 10] | ctrl | 2035 | 0.07
7.3 Direct electric firing | Direct electric heating | Financial data | Nominal investment (*total) [MEUR/MW] , from last update in 2019 | MEUR/MW | 2025 | E, H | [9, 10] | ctrl | 2040 | 0.07
7.3 Direct electric firing | Direct electric heating | Financial data | Nominal investment (*total) [MEUR/MW] , from last update in 2019 | MEUR/MW | 2025 | E, H | [9, 10] | ctrl | 2050 | 0.07
7.3 Direct electric firing | Direct electric heating | Financial data | Variable O&M [EUR/MWh] | EUR/MWh | 2025 | C |  | ctrl | 2025 | 0.235
7.3 Direct electric firing | Direct electric heating | Financial data | Variable O&M [EUR/MWh] | EUR/MWh | 2025 | C |  | ctrl | 2030 | 0.235
7.3 Direct electric firing | Direct electric heating | Financial data | Variable O&M [EUR/MWh] | EUR/MWh | 2025 | C |  | ctrl | 2035 | 0.235
7.3 Direct electric firing | Direct electric heating | Financial data | Variable O&M [EUR/MWh] | EUR/MWh | 2025 | C |  | ctrl | 2040 | 0.235
7.3 Direct electric firing | Direct electric heating | Financial data | Variable O&M [EUR/MWh] | EUR/MWh | 2025 | C |  | ctrl | 2050 | 0.235
7.3 Direct electric firing | Direct electric heating | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 9] | ctrl | 2025 | 0.01
7.3 Direct electric firing | Direct electric heating | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 9] | ctrl | 2030 | 0.01
7.3 Direct electric firing | Direct electric heating | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 9] | ctrl | 2035 | 0.01
7.3 Direct electric firing | Direct electric heating | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 9] | ctrl | 2040 | 0.01
7.3 Direct electric firing | Direct electric heating | Regulation ability | Cold start-up time [hours] | hours |  |  | [5, 9] | ctrl | 2050 | 0.01
7.3 Direct electric firing | Direct electric heating | Regulation ability | Minimum load [% of full load] | pct.offullload |  | D | 8 | ctrl | 2025 | 0.15
7.3 Direct electric firing | Direct electric heating | Regulation ability | Minimum load [% of full load] | pct.offullload |  | D | 8 | ctrl | 2030 | 0.15
7.3 Direct electric firing | Direct electric heating | Regulation ability | Minimum load [% of full load] | pct.offullload |  | D | 8 | ctrl | 2035 | 0.15
7.3 Direct electric firing | Direct electric heating | Regulation ability | Minimum load [% of full load] | pct.offullload |  | D | 8 | ctrl | 2040 | 0.15
7.3 Direct electric firing | Direct electric heating | Regulation ability | Minimum load [% of full load] | pct.offullload |  | D | 8 | ctrl | 2050 | 0.15
7.3 Direct electric firing | Direct electric heating | Regulation ability | Primary regulation (of full load, per 30 seconds) [%] | pct. |  | G | 11 | ctrl | 2025 | 1
7.3 Direct electric firing | Direct electric heating | Regulation ability | Primary regulation (of full load, per 30 seconds) [%] | pct. |  | G | 11 | ctrl | 2030 | 1
7.3 Direct electric firing | Direct electric heating | Regulation ability | Primary regulation (of full load, per 30 seconds) [%] | pct. |  | G | 11 | ctrl | 2035 | 1
7.3 Direct electric firing | Direct electric heating | Regulation ability | Primary regulation (of full load, per 30 seconds) [%] | pct. |  | G | 11 | ctrl | 2040 | 1
7.3 Direct electric firing | Direct electric heating | Regulation ability | Primary regulation (of full load, per 30 seconds) [%] | pct. |  | G | 11 | ctrl | 2050 | 1
7.3 Direct electric firing | Direct electric heating | Regulation ability | Secondary regulation (of full load, per minute) [%] | pct. |  | G | 11 | ctrl | 2025 | 1
7.3 Direct electric firing | Direct electric heating | Regulation ability | Secondary regulation (of full load, per minute) [%] | pct. |  | G | 11 | ctrl | 2030 | 1
7.3 Direct electric firing | Direct electric heating | Regulation ability | Secondary regulation (of full load, per minute) [%] | pct. |  | G | 11 | ctrl | 2035 | 1
7.3 Direct electric firing | Direct electric heating | Regulation ability | Secondary regulation (of full load, per minute) [%] | pct. |  | G | 11 | ctrl | 2040 | 1
7.3 Direct electric firing | Direct electric heating | Regulation ability | Secondary regulation (of full load, per minute) [%] | pct. |  | G | 11 | ctrl | 2050 | 1
7.3 Direct electric firing | Direct electric heating | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 9] | ctrl | 2025 | 0.01
7.3 Direct electric firing | Direct electric heating | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 9] | ctrl | 2030 | 0.01
7.3 Direct electric firing | Direct electric heating | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 9] | ctrl | 2035 | 0.01
7.3 Direct electric firing | Direct electric heating | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 9] | ctrl | 2040 | 0.01
7.3 Direct electric firing | Direct electric heating | Regulation ability | Warm start-up time [hours] | hours |  |  | [5, 9] | ctrl | 2050 | 0.01
7.3 Direct electric firing | Direct electric heating | Technology-specific data | Indirect investments cost [M€ per MW] | M€/MW |  | F |  | ctrl | 2025 | -
7.3 Direct electric firing | Direct electric heating | Technology-specific data | Indirect investments cost [M€ per MW] | M€/MW |  | F |  | ctrl | 2030 | -
7.3 Direct electric firing | Direct electric heating | Technology-specific data | Indirect investments cost [M€ per MW] | M€/MW |  | F |  | ctrl | 2035 | -
7.3 Direct electric firing | Direct electric heating | Technology-specific data | Indirect investments cost [M€ per MW] | M€/MW |  | F |  | ctrl | 2040 | -
7.3 Direct electric firing | Direct electric heating | Technology-specific data | Indirect investments cost [M€ per MW] | M€/MW |  | F |  | ctrl | 2050 | -
7.3 Direct electric firing | Direct electric heating | Technology-specific data | Non energy gains [M€ per MW] | M€/MW |  | F |  | ctrl | 2025 | -
7.3 Direct electric firing | Direct electric heating | Technology-specific data | Non energy gains [M€ per MW] | M€/MW |  | F |  | ctrl | 2030 | -
7.3 Direct electric firing | Direct electric heating | Technology-specific data | Non energy gains [M€ per MW] | M€/MW |  | F |  | ctrl | 2035 | -
7.3 Direct electric firing | Direct electric heating | Technology-specific data | Non energy gains [M€ per MW] | M€/MW |  | F |  | ctrl | 2040 | -
7.3 Direct electric firing | Direct electric heating | Technology-specific data | Non energy gains [M€ per MW] | M€/MW |  | F |  | ctrl | 2050 | -
7.3 Direct electric firing | Direct electric heating | Technology-specific data | Startup cost [€/MW/startup] | €/MW/startup |  | F |  | ctrl | 2025 | -
7.3 Direct electric firing | Direct electric heating | Technology-specific data | Startup cost [€/MW/startup] | €/MW/startup |  | F |  | ctrl | 2030 | -
7.3 Direct electric firing | Direct electric heating | Technology-specific data | Startup cost [€/MW/startup] | €/MW/startup |  | F |  | ctrl | 2035 | -
7.3 Direct electric firing | Direct electric heating | Technology-specific data | Startup cost [€/MW/startup] | €/MW/startup |  | F |  | ctrl | 2040 | -
7.3 Direct electric firing | Direct electric heating | Technology-specific data | Startup cost [€/MW/startup] | €/MW/startup |  | F |  | ctrl | 2050 | -
7.3 Direct electric firing | Direct electric heating | Technology-specific data | Temperature heat supply, maximum [°C] | °C |  |  | [4, 5] | ctrl | 2025 | 1800
7.3 Direct electric firing | Direct electric heating | Technology-specific data | Temperature heat supply, maximum [°C] | °C |  |  | [4, 5] | ctrl | 2030 | 2000
7.3 Direct electric firing | Direct electric heating | Technology-specific data | Temperature heat supply, maximum [°C] | °C |  |  | [4, 5] | ctrl | 2035 | 2000
7.3 Direct electric firing | Direct electric heating | Technology-specific data | Temperature heat supply, maximum [°C] | °C |  |  | [4, 5] | ctrl | 2040 | 2000
7.3 Direct electric firing | Direct electric heating | Technology-specific data | Temperature heat supply, maximum [°C] | °C |  |  | [4, 5] | ctrl | 2050 | 2000

## Notes
ws | description
2.a High temp. hp Up to 125C | - Total efficiency, net [%], nominel load. Based on a temperature lift of 100 K
2.b High temp. hp Up to 150 | - Total efficiency, net [%], nominel load. Based on a temperature lift of 100 K

## Ref
ws | description

## 1.1 Traditional heat pump
Technology |  | Heat pump, up to 60 °C, Temp lift = 40 K
year |  | 2025 | 2030 | 2035 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat generation capacity for one unit [MW] | 3 | 3 | 3 | 3 | 3 | 0.5 | 5 | 0.5 | 5 | A | [1, 2]
| Total efficiency, net [%], nominel load | 533% | 549% | 555% | 560% | 565.6% | 533% | 559.7% | 548.6% | 576.9% | B | [1, 3]
| Total efficiency, net [%], annual average | 528% | 544% | 550% | 555% | 560.6% | 528% | 554.7% | 543.6% | 571.9% | B,C
| Auxiliary electricity consumption [% of heat gen] | 1% | 1% | 1% | 1% | 1% | 1% | 4% | 1% | 4% |  | 2
| Forced outage [%] | 0% | 0% | 0% | 0% | 0% | 0% | 1% | 0% | 1% | D | 2
| Planned outage [weeks per year] | 1 | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | 2
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 | 15 | 40 | 15 | 40 |  | 2
| Construction time [years] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 1 | 0.3 | 1 |  | 2
Regulation Ability
| Minimum load [% of full load] | 25% | 25% | 25% | 25% | 25% | 10% | 50% | 10% | 50% |  | 2
| Warm start-up time [hours] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.2 |  | 2
| Cold start-up time [hours] | 1 | 1 | 1 | 1 | 1 | 0.2 | 1 | 0.2 | 1 |  | 2
Financial data
| Nominal investment [M€/MW] | 0.95 | 0.94 | 0.91 | 0.91 | 0.89 | 0.91 | 0.95 | 0.88 | 0.95 |  | 2
| - of which equipment [%] | 40% | 40% | 40% | 40% | 40% |  |  |  |  | E | 2
| - of which installation and other costs [%] | 60% | 60% | 60% | 60% | 60% |  |  |  |  | F | 2
| Fixed O&M [€/MJ/s/year] | 2127 | 2095 | 2032 | 2032 | 2001 | 2032 | 2127 | 1970 | 2127 |  | 2
| Variable O&M [€/MWh] | 3.07 | 3.02 | 2.93 | 2.93 | 2.89 | 2.93 | 3.07 | 2.84 | 3.07 |  | 2
Technology-specific data
| Indirect investments cost [M€/MW] | ctrl: 0.19; ctrl: 0.188; ctrl: 0.182; ctrl: 0.182; ctrl: 0.178; -: H
Non energy gains [M€/MW] | bar: ctrl to ctrl
| Startup cost [€/MW/startup] | ctrl: 10; ctrl: 10; ctrl: 10; ctrl: 10; ctrl: 10
| Temperature heat source supply [°C] | ctrl: 30; ctrl: 30; ctrl: 30; ctrl: 30; ctrl: 30; -: I
| Temperature heat source return [°C] | ctrl: 20; ctrl: 20; ctrl: 20; ctrl: 20; ctrl: 20; -: I
| - Total efficiency, net [%], nominel load. Based on a temperature lift of 50 K, 70°C max | 452% | 460% | 465% | 470% | 474% | 447% | 469% | 460% | 484% | G
| - Total efficiency, net [%], nominel load. Based on a temperature lift of 60 K, 80°C max | 395% | 400% | 404% | 408% | 412% | 388% | 407% | 399% | 420% | G
Cooling generation capacity for one unit [MW] | bar: ctrl to ctrl
Notes:
A | 0,5-5 MW
B | Estimated based on cases presented in [3]
C | Based on lost produktion during startup/shutdown
D | May vary depending on heat source availability
E | Very individual, can vary ÷ 20 %
F | Very individual, can vary + 20 %
G | Based on the old technology catalogue on process heat from 2020.
H | Going from current implementation to potential
I | Uses waste heat
References:
1 | Viegand Maagøe, 2019.
2 | Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2025
3 | EHPA, Large Scale heat pumps in Europe, 2019

## 1.2 heat_cool hp 80 C 75 K
Technology |  | Combined heating and cooling heat pump, up to 80 °C, Temp lift = 75 K
year |  | 2025 | 2030 | 2035 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat generation capacity for one unit [MW] | 3 | 3 | 3 | 3 | 3 | 0.5 | 5 | 0.5 | 5 | A | [1, 2]
| Total efficiency, net [%], nominel load | 335% | 343% | 348% | 349.9% | 353.4% | 333% | 351.8% | 342.8% | 360.4% | B | [1, 3]
| Total efficiency, net [%], annual average | 330% | 338% | 343% | 344.9% | 348.4% | 328% | 346.8% | 337.8% | 355.4% | B,C
| Auxiliary electricity consumption [% of heat gen] | 1% | 1% | 1% | 1% | 1% | 1% | 4% | 1% | 4% |  | 2
| Forced outage [%] | 0% | 0% | 0% | 0% | 0% | 0% | 1% | 0% | 1% | D | 2
| Planned outage [weeks per year] | 1 | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | 2
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 | 15 | 40 | 15 | 40 |  | 2
| Construction time [years] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 1 | 0.3 | 1 |  | 2
Regulation Ability
| Minimum load [% of full load] | 25% | 25% | 25% | 25% | 25% | 10% | 50% | 10% | 50% |  | 2
| Warm start-up time [hours] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.2 |  | 2
| Cold start-up time [hours] | 1 | 1 | 1 | 1 | 1 | 0.2 | 1 | 0.2 | 1 |  | 2
Financial data
| Nominal investment [M€/MW] | 0.95 | 0.94 | 0.91 | 0.91 | 0.89 | 0.91 | 0.95 | 0.88 | 0.95 |  | 2
| - of which equipment [%] | 40% | 40% | 40% | 40% | 40% |  |  |  |  | E | 2
| - of which installation and other costs [%] | 60% | 60% | 60% | 60% | 60% |  |  |  |  | F | 2
| Fixed O&M [€/MJ/s/year] | 2127 | 2095 | 2032 | 2032 | 2001 | 2032 | 2127 | 1970 | 2127 |  | 2
| Variable O&M [€/MWh] | 3.07 | 3.02 | 2.93 | 2.93 | 2.89 | 2.93 | 3.07 | 2.84 | 3.07 |  | 2
Technology-specific data
| Indirect investments cost [M€/MW] | ctrl: 0.19; ctrl: 0.188; ctrl: 0.182; ctrl: 0.182; ctrl: 0.178; -: H
Non energy gains [M€/MW] | bar: ctrl to ctrl
| Startup cost [€/MW/startup] | ctrl: 10; ctrl: 10; ctrl: 10; ctrl: 10; ctrl: 10
| Temperature heat source supply [°C] | ctrl: 15; ctrl: 15; ctrl: 15; ctrl: 15; ctrl: 15; -: I
| Temperature heat source return [°C] | ctrl: 5; ctrl: 5; ctrl: 5; ctrl: 5; ctrl: 5; -: I
| Cooling generation capacity for one unit [MW] | ctrl: -86.5522; ctrl: -84.4636; ctrl: -83.2069; ctrl: -82.7486; ctrl: -81.8996
Notes:
A | 0,5-5 MW
B | Estimated based on cases presented in [3]
C | Based on lost produktion during startup/shutdown
D | May vary depending on heat source availability
E | Very individual, can vary ÷ 20 %
F | Very individual, can vary + 20 %
G | Based on the old technology catalogue on process heat from 2020.
H | Going from current implementation to potential
I | Uses waste heat
References
1 | Viegand Maagøe, 2019.
2 | Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2025
3 | EHPA, Large Scale heat pumps in Europe, 2019

## 2.a High temp. hp Up to 125C
Technology |  | High-temperature heat pumps up to 125 °C
year |  | 2025 | 2030 | 2035 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat generation capacity for one unit [MW] | 2 | 2 | 3 | 3 | 3 | 0.3 | 25 | 0.2 | 50 | B | 4
| Total efficiency, net [%], nominel load. Based on a temperature lift of 65 K | 275% | 285% | 290% | 295% | 300% | 225% | 400% | 250% | 450% | C, H | 1
| Total efficiency, net [%], annual average | 270% | 280% | 285% | 290% | 295% | 220% | 395% | 245% | 445%
| Auxiliary electricity consumption [% of heat gen] | 2% | 2% | 2% | 2% | 2% | 1% | 7% | 1% | 7% |  | 1
| Forced outage [days] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  | 4
| Planned outage [weeks per year] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1 | 0 | 1 |  | 4
| Technical lifetime [years] | 20 | 20 | 20 | 20 | 20 | 15 | 30 | 15 | 30 | D | 4
| Construction time [years] | 0.6 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.8 | 0.2 | 0.8 | E | 4
| Space requirement [1000 m2/MW_e] | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.01 | 0.04 | 0.01 | 0.04
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 5% | 7% | 8% | 9% | 10% | 2% | 10% | 5% | 20%
| Secondary regulation (of full load, per minute) [] | 10% | 14% | 16% | 18% | 20% | 4% | 20% | 10% | 40%
| Minimum load (of full load) [] | 25% | 25% | 25% | 25% | 25% | 10% | 50% | 10% | 50% | F | 4
| Warm start-up time [hours] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.1 | 0.5 | 0.1 | 0.25 |  | 4
| Cold start-up time [hours] | 1 | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 |  | 4
Financial data
| Nominal investment (*total) [MEUR/MW] | 1.2 | 1.15 | 1.1 | 1.05 | 1 | 0.9 | 1.5 | 0.7 | 1.3 | G | [1, 4]
| - of which equipment [%] | 40% | 40% | 40% | 40% | 40% | 25% | 60% | 25% | 70% | A | 1
| - of which installation [%] | 60% | 60% | 60% | 60% | 60% | 40% | 75% | 30% | 75% | A | 3
| Fixed O&M [EUR/MW_y] | ctrl: 2494; ctrl: 2456; ctrl: 2382; ctrl: 2382; ctrl: 2345; -: 2
| Variable O&M [EUR/MWh] | ctrl: 3.6; ctrl: 3.54; ctrl: 3.43; ctrl: 3.43; ctrl: 3.39; -: 2
Technology-specific data
Technology dependent
| Indirect investment cost [M€/MW] | ctrl: 0.23; ctrl: 0.23; ctrl: 0.23; ctrl: 0.23; ctrl: 0.23; -: I
| - Steam generation decreases COP [%-point] | -15% | -10% | -5% | -5% | -5% | -5% | -20% | -5% | -15% |  | [1, 4]
| - Steam generation increases equipment cost by [MEUR/MW] | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.05 | 0.3 | 0.05 | 0.2 |  | [1, 4]
| - Additional equipment cost for temperature lift above 75 K [MEUR/MW] | 0.15 | 0.15 | 0.15 | 0.15 | 0.1 | 0.05 | 0.25 | 0.05 | 0.25 |  | [1, 4]
| - Total efficiency, net [%], nominel load. Based on a temperature lift of 40 K | 445% | 465% | 470% | 480% | 490% | 365% | 650% | 405% | 730% |  | [1, 4]
| - Total efficiency, net [%], nominel load. Based on a temperature lift of 80 K | 240% | 245% | 250% | 255% | 260% | 200% | 340% | 220% | 380% |  | [1, 4]
| - Total efficiency, net [%], nominel load. Based on a temperature lift of 100 K | 205% | 210% | 215% | 220% | 220% | 170% | 285% | 190% | 320% |  | [1, 4]
Notes:
A | Depends on production infrastructure. If HTHP replaces another HTHP, there will be lower investment in new installation
B | Unit sizes vary a lot and depends on production infrastructure. Lower capacities for specific production processes and higher capacities for central hot water supply
C | Efficiency depends on temperature lift of HTHP. High temperature lift reduces COP.
D | Both depends on lifetime of parts and new technology with higher efficiencies leading to replacement of existing systems
E | Expected to be lower in future when serial production is gaining traction
F | HTHPs are frequency controlled but typically a higher minimum load means smaller losses in COP
G | Expected to be lower in future due to serial production and better integration knowledge
H | Efficiency depends on technology of HTHP and production processes
I | Relevant when needing to install new hot water piping instead of existing steam piping. Assumed similar to gas boiler.
References:
1 | Danish Technological Institute
2 | Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2025
3 | Viegand Maagøe
4 | Annex 58
5 | Fraunhofer ISI, "Direct electrification of industrial process heat. An assessment of technologies, potentials and future prospects for the EU. Study on behalf of Agora Industry", 2024

## 2.b High temp. hp Up to 150
Technology |  | High-temperature heat pumps up to 150 °C
year |  | 2025 | 2030 | 2035 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat generation capacity for one unit [MW] | 2 | 2 | 3 | 3 | 3 | 0.5 | 80 | 0.5 | 100 | B | 4
| Total efficiency, net [%], nominel load. Based on a temperature lift of 65 K | 275% | 285% | 290% | 295% | 300% | 225% | 400% | 250% | 450% | C, H | 1
| Total efficiency, net [%], annual average | 270% | 280% | 285% | 290% | 295% | 220% | 395% | 245% | 445%
| Auxiliary electricity consumption [% of heat gen] | 2% | 2% | 2% | 2% | 2% | 1% | 7% | 1% | 7% |  | 1
| Forced outage [days] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  | 4
| Planned outage [weeks per year] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1 | 0 | 1 |  | 4
| Technical lifetime [years] | 20 | 20 | 20 | 20 | 20 | 15 | 30 | 15 | 30 | D | 4
| Construction time [years] | 0.6 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.8 | 0.2 | 0.8 | E | 4
| Space requirement [1000 m2/MW_e] | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.06 | 0.01 | 0.05
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 5% | 7% | 8% | 9% | 10% | 2% | 10% | 5% | 20%
| Secondary regulation (of full load, per minute) [] | 10% | 14% | 16% | 18% | 20% | 4% | 20% | 10% | 40%
| Minimum load (of full load) [] | 25% | 25% | 25% | 25% | 25% | 10% | 50% | 10% | 50% | F | 4
| Warm start-up time [hours] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.1 | 0.5 | 0.1 | 0.25 |  | 4
| Cold start-up time [hours] | 1 | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 |  | 4
Financial data
| Nominal investment (*total) [MEUR/MW] | 1.55 | 1.5 | 1.45 | 1.4 | 1.35 | 1.25 | 1.8 | 1.1 | 1.65 | G
| - of which equipment [%] | 40% | 40% | 40% | 40% | 40% | 25% | 60% | 25% | 70% | A | 1
| - of which installation [%] | 60% | 60% | 60% | 60% | 60% | 40% | 75% | 30% | 75% | A | 3
| Fixed O&M [EUR/MW_y], from last update in 2019 | ctrl: 2494; ctrl: 2456; ctrl: 2382; ctrl: 2382; ctrl: 2345; -: 2
| Variable O&M [EUR/MWh], from last update in 2019 | ctrl: 3.6; ctrl: 3.54; ctrl: 3.43; ctrl: 3.43; ctrl: 3.39; -: 1
Technology-specific data
Technology dependent
| Indirect investment cost [M€/MW] | ctrl: 0.23; ctrl: 0.23; ctrl: 0.23; ctrl: 0.23; ctrl: 0.23; -: I
| - Steam generation decreases COP [%-point] | -15% | -10% | -5% | -5% | -5% | -5% | -20% | -5% | -15% |  | [1, 4]
| - Steam generation increases equipment cost by [MEUR/MW] | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.05 | 0.3 | 0.05 | 0.2 |  | [1, 4]
| - Additional equipment cost for temperature lift above 75 K [MEUR/MW] | 0.2 | 0.2 | 0.15 | 0.15 | 0.15 | 0.1 | 0.3 | 0.1 | 0.35 |  | [1, 4]
| - Total efficiency, net [%], nominel load. Based on a temperature lift of 40 K | 445% | 465% | 470% | 480% | 490% | 365% | 650% | 405% | 730% |  | [1, 4]
| - Total efficiency, net [%], nominel load. Based on a temperature lift of 80 K | 240% | 245% | 250% | 255% | 260% | 200% | 340% | 220% | 380% |  | [1, 4]
| - Total efficiency, net [%], nominel load. Based on a temperature lift of 100 K | 205% | 210% | 215% | 220% | 220% | 170% | 285% | 190% | 320% |  | [1, 4]
Notes:
A | Depends on production infrastructure. If HTHP replaces another HTHP, there will be lower investment in new installation
B | Unit sizes vary a lot and depends on production infrastructure. Lower capacities for specific production processes and higher capacities for central hot water supply
C | Efficiency depends on temperature lift of HTHP. High temperature lift reduces COP.
D | Both depends on lifetime of parts and new technology with higher efficiencies leading to replacement of existing systems
E | Expected to be lower in future when serial production is gaining traction
F | HTHPs are frequency controlled but typically a higher minimum load means smaller losses in COP
G | Expected to be lower in future due to serial production and better integration knowledge
H | Efficiency depends on technology of HTHP and production processes
I | Relevant when needing to install new hot water piping instead of existing steam piping. Assumed similar to gas boiler.
References:
1 | Danish Technological Institute
2 | Jensen, J., Elmegaard, B., and Markussen, W. Industrial heat pumps for high temperature process applications.: A numerical study of the ammonia-water hybrid absorption-compression heat pump. PhD thesis. ,2016
3 | Viegand Maagøe
4 | Annex 58

## 4 MVR 5 K
Technology |  | Mechanical vapor recompression
year |  | 2025 | 2030 | 2035 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat generation capacity for one unit [MW] | 20 | 20 | 20 | 20 | 20 | 5 | 50 | 5 | 50 | A | 1
| Total efficiency, net [%], nominel load | 1260% | 1320% | 1350% | 1380% | 1430% | 1000% | 1512% | 1056% | 1716% | B | 1
| Total efficiency, net [%], annual average | 1210% | 1270% | 1300% | 1330% | 1380% | 950% | 1462% | 1006% | 1666%
| Auxiliary electricity consumption [% of heat gen] | 1% | 1% | 1% | 1% | 1% | 0% | 2% | 0% | 2% |  | 3
| Forced outage [%] | 0% | 0% | 0% | 0% | 0% | 0% | 1% | 0% | 1% |  | 2
| Planned outage [weeks per year] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1 | 0 | 1 |  | 2
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 | 15 | 35 | 15 | 35 |  | [1, 2]
| Construction time [years] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.2 | 0.05 | 0.2 |  | [1, 3]
Regulation Ability
| Minimum load [% of full load] | ctrl: 15%; ctrl: 15%; ctrl: 15%; ctrl: 15%; ctrl: 15%; -: 4
| Warm start-up time [hours] | ctrl: 0.5; ctrl: 0.5; ctrl: 0.5; ctrl: 0.5; ctrl: 0.5; -: 3
| Cold start-up time [hours] | ctrl: 1; ctrl: 1; ctrl: 1; ctrl: 1; ctrl: 1; -: 3
Financial data
| Nominal investment [M€/MW] | ctrl: 0.41; ctrl: 0.39; ctrl: 0.39; ctrl: 0.38; ctrl: 0.36; -: [1, 5]
| - of which equipment [%] | ctrl: 60%; ctrl: 60%; ctrl: 60%; ctrl: 60%; ctrl: 60%; -: [1, 5]
| - of which installation [%] | ctrl: 40%; ctrl: 40%; ctrl: 40%; ctrl: 40%; ctrl: 40%; -: [1, 5]
| Fixed O&M [€/MJ/s/year] | ctrl: 2345; ctrl: 2345; ctrl: 2345; ctrl: 2345; ctrl: 2345; -: 2
| Variable O&M [€/MWh] | ctrl: 2.1; ctrl: 2; ctrl: 2; ctrl: 2; ctrl: 1.9; -: 2
Notes:
A | 5-50 MW
B | Assumed temperature lift of 5 K (saturation temperatur)
References:
1 | Viegand Maagøe, MVR, 2018
2 | Technological data for energi plants (Compressions Heat Pumps for DH), Energistyrelsen, 2017
3 | Viegand Maagøe, 2019
4 | EPCON, EVAPORATION TECHNOLOGY, 2019
5 | EPCON investment cost offer, 2017.

## 5.1a Electric boiler steam
Technology |  | Electric boiler, 0,4-0,69 kV, steam, 1-12 bar
year |  | 2025 | 2030 | 2035 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat generation capacity for one unit [MW] | 2 | 2 | 2 | 2 | 2 | 1 | 5 | 1 | 5 | A
| Total efficiency, net [%], nominel load | 99% | 99% | 99% | 99% | 99% | 98% | 100% | 98% | 100% |  | [1, 2]
| Total efficiency, net [%], annual average | 99% | 99% | 99% | 99% | 99% | 98% | 99% | 98% | 99% |  | [1, 2]
| Auxiliary electricity consumption [% of heat gen] | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.1% | 0.5% | 0.1% | 0.5% |  | [1, 2]
| Forced outage [%] | 1% | 1% | 1% | 1% | 1% | 0.5% | 1% | 0.5% | 1% |  | [1, 2]
| Planned outage [weeks per year] | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | 2
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 | 20 | 25 | 20 | 25 |  | 2
| Construction time [years] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 1 |  | 1
Regulation Ability
| Minimum load [% of full load] | ctrl: 2%; ctrl: 2%; ctrl: 2%; ctrl: 2%; ctrl: 2%; -: 2
| Warm start-up time [hours] | ctrl: 0.03; ctrl: 0.03; ctrl: 0.03; ctrl: 0.03; ctrl: 0.03; -: 2
| Cold start-up time [hours] | ctrl: 0.17; ctrl: 0.17; ctrl: 0.17; ctrl: 0.17; ctrl: 0.17; -: 2
Financial data
| Nominal investment [M€/MW] | 0.25 | 0.22 | 0.22 | 0.22 | 0.22 |  |  |  |  | B,C | [1, 2, 4]
| - of which equipment [%] | ctrl: 75%; ctrl: 75%; ctrl: 75%; ctrl: 75%; ctrl: 75%; -: [2, 4]
| - of which installation [%] | ctrl: 25%; ctrl: 25%; ctrl: 25%; ctrl: 25%; ctrl: 25%; -: [2, 4]
| Fixed O&M [€/MJ/s/year] | ctrl: 1442; ctrl: 1375; ctrl: 1341; ctrl: 1307; ctrl: 1240; -: [2, 3, 4]
| Variable O&M [€/MWh] | ctrl: 0.674; ctrl: 0.642; ctrl: 0.627; ctrl: 0.611; ctrl: 0.578; -: [2, 3, 4]
Technology-specific data
| Additional investments cost for 12-16 bar boilers [M€/MW] | ctrl: 0.064; ctrl: 0.057; ctrl: 0.057; ctrl: 0.057; ctrl: 0.057
Notes:
A | 1-5 MW
B | Electrode boilers at low voltage typically needs a transformer from distribution grid. Costs for the transformer are included in the equipment costs.
C | Investment cost is slightly higher than for a hot water boiler.
References:
1 | Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2022
2 | AS:scan, Personal communication, 2022
3 | Tjæreborg Industri, Personal communication, 2022
4 | Nordheat, Personal communication, 2022

## 5.1b Electric boiler steam
Technology |  | Electric boiler, 10 kV, steam, 1-12 bar
year |  | 2025 | 2030 | 2035 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat generation capacity for one unit [MW] | 15 | 15 | 15 | 15 | 15 | 5 | 60 | 5 | 60 | A
| Total efficiency, net [%], nominel load | 99% | 99% | 99% | 99% | 99% | 98% | 100% | 98% | 100% |  | [1, 2]
| Total efficiency, net [%], annual average | 99% | 99% | 99% | 99% | 99% | 98% | 99% | 98% | 99% |  | [1, 2]
| Auxiliary electricity consumption [% of heat gen] | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.1% | 0.5% | 0.1% | 0.5% |  | [1, 2]
| Forced outage [%] | 1% | 1% | 1% | 1% | 1% | 0.5% | 1% | 0.5% | 1% |  | [1, 2]
| Planned outage [weeks per year] | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | 2
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 | 20 | 25 | 20 | 25 |  | 2
| Construction time [years] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 1 |  | 1
Regulation Ability
| Minimum load [% of full load] | ctrl: 2%; ctrl: 2%; ctrl: 2%; ctrl: 2%; ctrl: 2%; -: 2
| Warm start-up time [hours] | ctrl: 0.03; ctrl: 0.03; ctrl: 0.03; ctrl: 0.03; ctrl: 0.03; -: 2
| Cold start-up time [hours] | ctrl: 0.17; ctrl: 0.17; ctrl: 0.17; ctrl: 0.17; ctrl: 0.17; -: 2
Financial data
| Nominal investment [M€/MW] | 0.11 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  |  | B,C | [1, 2, 4]
| - of which equipment [%] | ctrl: 85%; ctrl: 85%; ctrl: 85%; ctrl: 85%; ctrl: 85%; -: 2
| - of which installation [%] | ctrl: 15%; ctrl: 15%; ctrl: 15%; ctrl: 15%; ctrl: 15%; -: 2
| Fixed O&M [€/MJ/s/year] | ctrl: 1298; ctrl: 1237; ctrl: 1208; ctrl: 1177; ctrl: 1116; -: [2, 3, 4]
| Variable O&M [€/MWh] | ctrl: 0.61; ctrl: 0.58; ctrl: 0.56; ctrl: 0.55; ctrl: 0.52; -: [2, 3, 4]
Technology-specific data
| Additional investments cost for 12-16 bar boilers [M€/MW] | ctrl: 0.021; ctrl: 0.018; ctrl: 0.018; ctrl: 0.018; ctrl: 0.018
Notes:
A | 5-60 MW
B | Electrode boilers at medium-high voltage are directly connected to the distribution grid. Costs for the distribution board are included in the equipment costs.
C | Investment cost is slightly higher than for a hot water boiler.
References:
1 | Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2022
2 | AS:scan, Personal communication, 2022
3 | Tjæreborg Industri, Personal communication, 2022
4 | Nordheat, Personal communication, 2022

## 5.2a Electric boiler hot wate
Technology |  | Electric boiler, 0,4-0,69 kV, hot water, 1-12 bar
year |  | 2025 | 2030 | 2035 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat generation capacity for one unit [MW] | 2 | 2 | 2 | 2 | 2 | 1 | 5 | 1 | 5 | A
| Total efficiency, net [%], nominel load | 99% | 99% | 99% | 99% | 99% | 98% | 100% | 98% | 100% |  | [1, 2]
| Total efficiency, net [%], annual average | 99% | 99% | 99% | 99% | 99% | 98% | 99% | 98% | 99% |  | [1, 2]
| Auxiliary electricity consumption [% of heat gen] | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.1% | 0.5% | 0.1% | 0.5% |  | [1, 2]
| Forced outage [%] | 1% | 1% | 1% | 1% | 1% | 0.5% | 1% | 0.5% | 1% |  | [1, 2]
| Planned outage [weeks per year] | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | 1
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 | 20 | 25 | 20 | 25 |  | 2
| Construction time [years] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 1 |  | 1
Regulation Ability
Minimum load [% of full load] | bar: ctrl to ctrl; -
| Warm start-up time [hours] | ctrl: 0.008; ctrl: 0.008; ctrl: 0.008; ctrl: 0.008; ctrl: 0.008; -: 1
| Cold start-up time [hours] | ctrl: 0.08; ctrl: 0.08; ctrl: 0.08; ctrl: 0.08; ctrl: 0.08; -: 1
Financial data
| Nominal investment [M€/MW] | 0.202 | 0.187 | 0.187 | 0.187 | 0.187 |  |  |  |  | B,C | [1, 2, 4]
| - of which equipment [%] | ctrl: 75%; ctrl: 75%; ctrl: 75%; ctrl: 75%; ctrl: 75%; -: 2
| - of which installation [%] | ctrl: 25%; ctrl: 25%; ctrl: 25%; ctrl: 25%; ctrl: 25%; -: 2
| Fixed O&M [€/MJ/s/year] | ctrl: 1254; ctrl: 1196; ctrl: 1166; ctrl: 1137; ctrl: 1079; -: 1
| Variable O&M [€/MWh] | ctrl: 0.59; ctrl: 0.56; ctrl: 0.54; ctrl: 0.53; ctrl: 0.5; -: [2, 3, 4]
Technology-specific data
| Indirect investments cost [M€/MW] | ctrl: 0.101; ctrl: 0.0935; ctrl: 0.0935; ctrl: 0.0935; ctrl: 0.0935; -: D
| Additional investments cost for 12-16 bar boilers [M€/MW] | ctrl: 0.057; ctrl: 0.049; ctrl: 0.049; ctrl: 0.049; ctrl: 0.049
Notes:
A | 1-5 MW
B | Electrode boilers at low voltage typically needs a transformer from distribution grid. Costs for the transformer are included in the equipment costs.
C | Investment cost is slightly lower than for a steam boiler.
D | Going from current implementation to potential
References:
1 | Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2022
2 | AS:scan, Personal communication, 2022
3 | Tjæreborg Industri, Personal communication, 2019
4 | Nordheat, Personal communication, 2022

## 5.2b Electric boiler hot wate
Technology |  | Electric boiler,10 kV, hot water, 1-12 bar
year |  | 2025 | 2030 | 2035 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat generation capacity for one unit [MW] | 15 | 15 | 15 | 15 | 15 | 5 | 60 | 5 | 60 | A
| Total efficiency, net [%], nominel load | 99% | 99% | 99% | 99% | 99% | 98% | 100% | 98% | 100% |  | [1, 2]
| Total efficiency, net [%], annual average | 99% | 99% | 99% | 99% | 99% | 98% | 99% | 98% | 99% |  | [1, 2]
| Auxiliary electricity consumption [% of heat gen] | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.1% | 0.5% | 0.1% | 0.5% |  | [1, 2]
| Forced outage [%] | 1% | 1% | 1% | 1% | 1% | 0.5% | 1% | 0.5% | 1% |  | [1, 2]
| Planned outage [weeks per year] | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | 1
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 | 20 | 25 | 20 | 25 |  | 2
| Construction time [years] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 1 |  | 1
Regulation Ability
Minimum load [% of full load] | bar: ctrl to ctrl; -
| Warm start-up time [hours] | ctrl: 0.008; ctrl: 0.008; ctrl: 0.008; ctrl: 0.008; ctrl: 0.008; -: 1
| Cold start-up time [hours] | ctrl: 0.08; ctrl: 0.08; ctrl: 0.08; ctrl: 0.08; ctrl: 0.08; -: 1
Financial data
| Nominal investment [M€/MW] | 0.089 | 0.084 | 0.084 | 0.084 | 0.084 |  |  |  |  | B,C | [1, 2, 4]
| - of which equipment [%] | ctrl: 85%; ctrl: 85%; ctrl: 85%; ctrl: 85%; ctrl: 85%; -: 2
| - of which installation [%] | ctrl: 15%; ctrl: 15%; ctrl: 15%; ctrl: 15%; ctrl: 15%; -: 2
| Fixed O&M [€/MJ/s/year] | ctrl: 1103; ctrl: 1076; ctrl: 1050; ctrl: 1023; ctrl: 971; -: [1, 2, 4]
| Variable O&M [€/MWh] | ctrl: 0.53; ctrl: 0.5; ctrl: 0.49; ctrl: 0.48; ctrl: 0.45; -: [2, 3, 4]
Technology-specific data
| Indirect investments cost [M€/MW] | ctrl: 0.0445; ctrl: 0.042; ctrl: 0.042; ctrl: 0.042; ctrl: 0.042; -: D
| Additional investments cost for 12-16 bar boilers [M€/MW] | ctrl: 0.018; ctrl: 0.016; ctrl: 0.016; ctrl: 0.016; ctrl: 0.016
Notes:
A | 5-60 MW
B | Electrode boilers at medium-high voltage are directly connected to the distribution grid. Costs for the distribution board are included in the equipment costs.
C | Investment cost is slightly lower than for a steam boiler.
D | Going from current implementation to potential
References:
1 | Danish Enegy Agency, Technology Data - Energy Plants for Electricity and District heating generation, 2022
2 | AS:scan, Personal communication, 2022
3 | Tjæreborg Industri, Personal communication, 2022
4 | Nordheat, Personal communication, 2022

## 6.1 Boiler, gas and oil
Technology |  | Boiler, gas and oil
year |  | 2025 | 2030 | 2035 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat generation capacity for one unit [MW] | 5 | 5 | 5 | 5 | 5 | 0.5 | 50 | 0.5 | 50 |  | [1, 2, 3, 6]
| Total efficiency, net [%], nominel load | 94% | 94% | 94% | 94% | 94% | 92% | 95% | 92% | 95% | A, B, E | [1, 4, 6]
| Total efficiency, net [%], annual average | 93.9% | 93.9% | 93.9% | 93.9% | 93.9% | 91.9% | 94.9% | 91.9% | 94.9% | A, B, D | [1, 4]
| Auxiliary electricity consumption [% of heat gen] | 0.15% | 0.15% | 0.15% | 0.15% | 0.15% | 0% | 0.15% | 0% | 0.15% |  | [1, 2]
| Forced outage [%] | 1% | 1% | 1% | 1% | 1% | 0% | 2% | 0% | 2% |  | 1
| Planned outage [weeks per year] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.6 | 0.3 | 0.6 |  | [1, 2]
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 |  |  | 1
| Construction time [years] | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.02 | 0.7 | 0.02 | 0.7 |  | [1, 2]
| Space requirement [1000 m2/MW_e] | 0.008 | 0.008 | 0.008 | 0.008 | 0.008 | 0.007 | 0.01 | 0.007 | 0.01 |  | [2, 3]
Regulation ability
| Primary regulation (of full load, per 30 seconds) [%] | 15% | 15% | 15% | 15% | 15% | 3.5% | 30% |  |  | H | [1, 2, 6]
| Secondary regulation (of full load, per minute) [%] | 30% | 30% | 30% | 30% | 30% | 7% | 60% |  |  | H | [1, 2, 6]
| Minimum load (of full load) [%] | 15% | 15% | 15% | 15% | 15% | 10% | 20% |  |  |  | [1, 2, 6]
| Warm start-up time [hours] | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.025 | 0.2 |  |  |  | [1, 2, 6]
| Cold start-up time [hours] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 1 |  |  |  | [1, 2, 6]
Financial data
| Nominal investment (*total) [MEUR/MW] | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 |  |  |  |  | C, B | [1, 2, 6]
| - of which equipment [%] | ctrl: 66%; ctrl: 66%; ctrl: 66%; ctrl: 66%; ctrl: 66%; -: [1, 2]
| - of which installation [%] | ctrl: 34%; ctrl: 34%; ctrl: 34%; ctrl: 34%; ctrl: 34%; -: [1, 2]
| Fixed O&M [EUR/MW_y] | ctrl: 2000; ctrl: 2000; ctrl: 2000; ctrl: 2000; ctrl: 2000; -: [1, 2]
| Variable O&M [EUR/MWh] | ctrl: 1.23; ctrl: 1.23; ctrl: 1.23; ctrl: 1.23; ctrl: 1.23; -: 1
Technology-specific data
| Indirect investment cost [M€/MW] | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 |  |  |  |  | J | 2
Technology dependent
| - Adding flue gas condenser (after economiser) increases efficiency by [%-point] (gas only) | 6% | 6% | 6% | 6% | 6% |  |  |  |  | I, E | [1, 2, 5]
| - Adding flue gas condenser (after economiser) increases nominal investment by [%] (gas only) | 10% | 10% | 10% | 10% | 10% |  |  |  |  | I | 2
- Hot water boiler instead of steam boiler increases efficiency by [%-point] | bar: ctrl to ctrl; -
| - Hot water boiler instead of steam boiler reduces nominal investment by [%] | 30% | 30% | 30% | 30% | 30% |  |  |  |  | G | [2, 3]
Notes:
A | Effeciency for unit with economiser (but not flue gas condenser) installed.
B | Values for steam boiler (see technology-specific data for differences with hot water boiler)
C | Prices include boiler, firing equipment, pumps, economiser, water-treatment system, chimney and installation.
D | Assuming 10 starts a year.
E | For condensing boilers, efficiencies above 100% are possible, since the standard efficiency calculation using the lower heating value (LHV) as denominator.
F | 1 %-point higher for hot water boiler, due to assumed lower flue gas temperature. If no flue gas condenser and economiser is used, the increase will be higher.
G | Hot water boiler is generally operating at lower pressure levels, so pressure vessel is cheaper. Water treatment system not necessary for hot water boiler.
H | Assumes warm operation.
I | Flue gas condenser not possible for oil boilers as its combustion products contain pollutants which would heavily corrode the heat exchanger surfaces if condensed.
J | Relevant for hot water boiler when needing to install new hot water piping instead of existing steam piping.
References:
1 | Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2025) ."44 Natural Gas DH Only"
2 | Bosch Industrial, Personal correspondence & product catalogue, 2025
3 | Viessmann, Personal correspondence & product catalogue, 2025
4 | Vakklianainen, Esa. Steam Generation from Biomass. 2017. (Chapter 3, Boiler processes)
5 | Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., Swithenbank, J. Condensing boiler applications in the process industry. Applied Energy, 89, 30-36, 2012
6 | Danstoker, Personal correspondence & product catalogue, 2025

## 6.2 Boiler, biomass
Technology |  | Boiler, biomass
year |  | 2025 | 2030 | 2035 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat generation capacity for one unit [MW] | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 0.3 | 50 | 0.3 | 50 |  | [1, 4, 5]
| Total efficiency, net [%], nominel load | 89% | 89% | 89% | 89% | 89% | 87% | 91% | 87% | 91% | A, B | 2
| Total efficiency, net [%], annual average | 88.9% | 88.9% | 88.9% | 88.9% | 88.9% | 86.9% | 90.9% | 86.9% | 90.9% | A, B, D | 2
Auxiliary electricity consumption [% of heat gen] | bar: ctrl to upper; -
Forced outage [%] | bar: ctrl to upper; -
| Planned outage [weeks per year] | 2 | 2 | 2 | 2 | 2 | 1.7 | 2.3 | 1.5 | 2.5 |  | 1
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 1 | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 |  | 1
| Space requirement [1000 m2/MW_e] | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.14 | 0.25 | 0.12 | 0.27 |  | 1
Regulation ability
Primary regulation (of full load, per 30 seconds) [%]
| Secondary regulation (of full load, per minute) [%] | ctrl: 10%; ctrl: 10%; ctrl: 10%; ctrl: 10%; ctrl: 10%; -: 1
| Minimum load (of full load) [%] | ctrl: 20%; ctrl: 20%; ctrl: 20%; ctrl: 20%; ctrl: 20%; -: 1
| Warm start-up time [hours] | ctrl: 0.25; ctrl: 0.25; ctrl: 0.25; ctrl: 0.25; ctrl: 0.25; -: 1
| Cold start-up time [hours] | ctrl: 0.5; ctrl: 0.5; ctrl: 0.5; ctrl: 0.5; ctrl: 0.5; -: 1
Financial data
| Nominal investment (*total) [MEUR/MW] | ctrl: 0.87841; ctrl: 0.82892; ctrl: 0.80727; ctrl: 0.78562; ctrl: 0.74232; -: 1
| - of which equipment [%] | ctrl: 60%; ctrl: 60%; ctrl: 60%; ctrl: 60%; ctrl: 60%; -: 1
| - of which installation [%] | ctrl: 40%; ctrl: 40%; ctrl: 40%; ctrl: 40%; ctrl: 40%; -: 1
| Fixed O&M [EUR/MW_y] | ctrl: 39500; ctrl: 38700; ctrl: 37900; ctrl: 37100; ctrl: 35600; -: 1
| Variable O&M [EUR/MWh] | 1.45 | 1.45 | 1.45 | 1.45 | 1.45 |  |  |  |  | C, H | 1
Technology-specific data
| Indirect investment cost [M€/MW] | ctrl: 0.23; ctrl: 0.23; ctrl: 0.23; ctrl: 0.23; ctrl: 0.23; -: K, J
Technology dependent
| - Using wood chips, and adding flue gas condenser (after economiser) increases efficiency by [%-point] | 25% | 25% | 25% | 25% | 25% |  |  |  |  | F, E | [1, 3]
| - Using wood pellets, and adding flue gas condenser (after economiser) increases efficiency by [%-point] | 12% | 12% | 12% | 12% | 12% |  |  |  |  | E, I | [1, 3]
- Hot water boiler instead of steam boiler increases efficiency by [%-point] | bar: ctrl to ctrl; -
| - Wood pellets (instead of wood chips) reduces Variable O&M by [%] | ctrl: 50%; ctrl: 50%; ctrl: 50%; ctrl: 50%; ctrl: 50%; -: 1
Notes:
A | Effeciency for unit with economiser (but not flue gas condenser) installed.
B | Values for steam boiler (see technology-specific data for differences with hot water boiler)
C | Values for wood chips (see technology-specific data for differences with wood pellets)
D | Assuming 10 starts a year.
E | For condensing boilers, efficiencies above 100% are possible, since the standard efficiency calculation using the lower heating value (LHV) as denominator.
F | Large increase in efficiency using flue gas condensen because of large water content in wood chips.
G | 1 %-point higher for hot water boiler, due to assumed lower flue gas temperature
H | Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost
I | Wood pellets have lower water content than wood chips, and therefore the advantage of using flue gas condensation is smaller.
J | Assumed similar to gas and oil boiler.
K | Relevant for hot water boiler when needing to install new hot water piping instead of existing steam piping.
References:
1 | Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2025) ." 09a Wood Chips HOP (heat-only plant), small" and "09b Wood Pellets HOP"
2 | Vakklianainen, Esa. Steam Generation from Biomass. 2017. (Chapter 3, Boiler processes)
3 | Chen, Q., Finney, K., Li, H., Zhang, X., Zhou, J., Sharifi, V., Swithenbank, J. Condensing boiler applications in the process industry. Applied Energy, 89, 30-36, 2012
4 | Tjæreborg Industri, Referenceliste for fasbrændselsanlæg (Reference list for solid fuel plants), 2024
5 | Danstoker product catalogue, 2025

## 6.3 Boiler, coal
Technology |  | Boiler, coal
year |  | 2025 | 2030 | 2035 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat generation capacity for one unit [MW] | 5 | 5 | 5 | 5 | 5 | 1.6 | 50 | 1.6 | 50 |  | [3, 4]
| Total efficiency, net [%], nominel load | 90% | 90% | 90% | 90% | 90% | 88% | 92% | 88% | 92% | A, B, C | 2
| Total efficiency, net [%], annual average | 89.9% | 89.9% | 89.9% | 89.9% | 89.9% | 87.9% | 91.9% | 87.9% | 91.9% | A, B, C, D | 2
| Auxiliary electricity consumption [% of heat gen] | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | F | 1
| Forced outage [%] | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | F | 1
| Planned outage [weeks per year] | 2 | 2 | 2 | 2 | 2 | 1.7 | 2.3 | 1.5 | 2.5 | F | 1
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 | E, F | 1
| Construction time [years] | 1 | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 | F | 1
| Space requirement [1000 m2/MW_e] | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.14 | 0.25 | 0.12 | 0.27 | F | 1
Regulation ability
Primary regulation (of full load, per 30 seconds) [%]
| Secondary regulation (of full load, per minute) [%] | 10% | 10% | 10% | 10% | 10% |  |  |  |  | F | 1
| Minimum load (of full load) [%] | 15% | 15% | 15% | 15% | 15% |  |  |  |  | E | 1
| Warm start-up time [hours] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  |  | F | 1
| Cold start-up time [hours] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  |  | F | 1
Financial data
| Nominal investment (*total) [MEUR/MW] | 0.565 | 0.545 | 0.533 | 0.521 | 0.515 |  |  |  |  | F, H | 1
| - of which equipment [%] | ctrl: 60%; ctrl: 60%; ctrl: 60%; ctrl: 60%; ctrl: 60%; -: 1
| - of which installation [%] | ctrl: 40%; ctrl: 40%; ctrl: 40%; ctrl: 40%; ctrl: 40%; -: 1
| Fixed O&M [EUR/MW_y] | 40000 | 39500 | 39000 | 38500 | 37500 |  |  |  |  | E, F | 1
| Variable O&M [EUR/MWh] | 1.45 | 1.45 | 1.45 | 1.45 | 1.45 |  |  |  |  | F | 1
Technology-specific data
| Indirect investment cost [M€/MW] | ctrl: 0.23; ctrl: 0.23; ctrl: 0.23; ctrl: 0.23; ctrl: 0.23; -: I, J
Technology dependent
- Hot water boiler instead of steam boiler increases efficiency by [%-point] | bar: ctrl to ctrl; -
Notes:
A | Effeciency for unit with economiser (but not flue gas condenser) installed.
B | Values for steam boiler (see technology-specific data for differences with hot water boiler)
C | Flue gas condenser not possible for coal boiler, since no water vapor is present in flue gas.
D | Assuming 10 starts a year.
E | Values estimated based on "01 Coal CHP" from ref. 1.
F | Values estimated based on "09b Wood Pellets HOP"/"09a Wood Chips HOP, small" from ref. 1 (since they are solid fuels, and often the same boiler can used either biomass or coal)
G | 1 %-point higher for hot water boiler, due to assumed lower flue gas temperature
H | Viegand Maagøe A/S experience
I | Relevant for hot water boiler when needing to install new hot water piping instead of existing steam piping.
J | Assumed similar to gas and oil boiler.
References:
1 | Danish Energy Agency, Energy Plants for Electricity and District heating generation, 2016 (updated 2025).
2 | Vakklianainen, Esa. Steam Generation from Biomass. 2017. (Chapter 3, Boiler processes)
3 | Tjæreborg Industri, Referenceliste for fasbrændselsanlæg (Reference list for solid fuel plants), 2024
4 | Danstoker product catalogue, 2025

## 7.1 Direct firing Natural Gas
Technology |  | Direct firing, Natural gas
year |  | 2025 | 2030 | 2035 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat generation capacity for one unit [MW] | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 1 | 10 | 1 | 10 |  | 2
| Total efficiency, net [%], nominel load | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | A | 2
| Total efficiency, net [%], annual average | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | A | 2
| Auxiliary electricity consumption [% of heat gen] | 0.25% | 0.25% | 0.25% | 0.25% | 0.25% | 0.1% | 1% | 0.1% | 1% |  | [8, 9]
| Forced outage [%] | 0.25% | 0.25% | 0.25% | 0.25% | 0.25% | 0% | 0.5% | 0% | 0.5% |  | 2
| Planned outage [weeks per year] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1 | 0 | 1 |  | 2
| Technical lifetime [years] | 15 | 15 | 15 | 15 | 15 | 10 | 20 | 10 | 20 |  | 4
| Construction time [years] | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.04 | 0.01 | 0.04 |  | 2
Regulation Ability
| Minimum load [% of full load] | ctrl: 10%; ctrl: 10%; ctrl: 10%; ctrl: 10%; ctrl: 10%; -: 6
| Warm start-up time [hours] | ctrl: 0.01; ctrl: 0.01; ctrl: 0.01; ctrl: 0.01; ctrl: 0.01; -: 2
| Cold start-up time [hours] | ctrl: 0.01; ctrl: 0.01; ctrl: 0.01; ctrl: 0.01; ctrl: 0.01; -: 2
Environment
| SO2 [g per GJ fuel] | ctrl: 0.3; ctrl: 0.3; ctrl: 0.3; ctrl: 0.3; ctrl: 0.3; -: 1
| PM2.5 [g per GJ fuel] | ctrl: 0.1; ctrl: 0.1; ctrl: 0.1; ctrl: 0.1; ctrl: 0.1; -: 1
| NOX [g per GJ fuel] | ctrl: 9; ctrl: 7; ctrl: 7; ctrl: 6; ctrl: 6; -: 1
| CH4 [g per GJ fuel] | ctrl: 3; ctrl: 2; ctrl: 2; ctrl: 2; ctrl: 2; -: 1
N2O [g per GJ fuel] | bar: ctrl to ctrl; -
Financial data
| Nominal investment [M€/MW] | 0.0176 | 0.0176 | 0.0176 | 0.0176 | 0.0176 |  |  |  |  | B | [4, 7]
| - of which equipment [%] | ctrl: 66.67%; ctrl: 66.67%; ctrl: 66.67%; ctrl: 66.67%; ctrl: 66.67%; -: 7
| - of which installation [%] | ctrl: 33.33%; ctrl: 33.33%; ctrl: 33.33%; ctrl: 33.33%; ctrl: 33.33%; -: 7
| Fixed O&M [€/MJ/s/year] | 213 | 208 | 205 | 202 | 181 |  |  |  |  | C | [2, 1]
| Variable O&M [€/MWh] | 0.117 | 0.105 | 0.105 | 0.105 | 0.105 |  |  |  |  | C | 1
Technology-specific data
Indirect investments cost [M€/MW] | bar: ctrl to ctrl; - to -
Notes:
A | The efficiency of the burner is set equal to the lower heating value, the process will determine how well the flue gas is utilised, and thus the final efficiency.
B | Unit price is based on Miton Megatherms 2.5 MW burner, installed price assessed by Viegand Maagøe. The assessment is an experience based guess as no concrete data was retrieved.
C | Assumed to be equal to 10% of the boiler O&M from [1].
D | The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 73, 2030: 75, 2040: 76, 2050: 76. Includes transport tarif
E | The indirect costs will be too strong a function of the process to put into a single value across all industries.
References:
1 | Danish Energy Agency, Technology Data Generation of Electricity and District Heating, August 2016 - Updated November 2019
2 | Viegand Maagøe, Direct Firing, 2018
3 | Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
4 | Milton Megatherm, Correspondance 2019
5 | IOGP, The potential for CCS and CCU in Europe, REPORT TO THE THIRTY SECOND MEETING OF THE EUROPEAN GAS REGULATORY FORUM 5-6 JUNE 2019
6 | Eclipse, Vortometric Burner Series Datasheet 128-3, 20/2/2015
7 | Viegand Maagøe assessment, 2019
8 | Eclipse, Eclipse AirHeat Burners Datasheet 115-11, 30/9/2010
9 | Eclipse, Eclipse RatioAir Burners Datasheet 135, 21/10/2010

## 7.2 Direct firing Solid Fuels
Technology |  | Direct firing, Solid fuels
year |  | 2025 | 2030 | 2035 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat generation capacity for one unit [MW] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
| Total efficiency, net [%], nominel load | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | A | 2
| Total efficiency, net [%], annual average | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | A | 2
| Auxiliary electricity consumption [% of heat gen] | 0.25% | 0.25% | 0.25% | 0.25% | 0.25% | 0.1% | 1% | 0.1% | 1% | B | [8, 9]
| Forced outage [%] | 0.25% | 0.25% | 0.25% | 0.25% | 0.25% | 0% | 0.5% | 0% | 0.5% |  | 2
| Planned outage [weeks per year] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 2 | 5 | 2 | 5 |  | 4
| Technical lifetime [years] | 15 | 15 | 15 | 15 | 15 | 10 | 20 | 10 | 20 |  | [2, 4]
| Construction time [years] | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.001 | 0.015 | 0.001 | 0.015 | I | [2, 4]
Regulation Ability
| Minimum load [% of full load] | ctrl: 10%; ctrl: 10%; ctrl: 10%; ctrl: 10%; ctrl: 10%; -: 6
| Warm start-up time [hours] | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 |  |  |  |  | F | 2
| Cold start-up time [hours] | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 |  |  |  |  | F | 2
Environment
SO2 [g per GJ fuel] | bar: -
PM2.5 [g per GJ fuel] | bar: -
NOX [g per GJ fuel] | bar: -
CH4 [g per GJ fuel] | bar: -
N2O [g per GJ fuel] | bar: -
Financial data
| Nominal investment [M€/MW] | 0.258 | 0.258 | 0.258 | 0.258 | 0.258 |  |  |  |  | E, G, H | [4, 7]
| - of which equipment [%] | ctrl: 66.67%; ctrl: 66.67%; ctrl: 66.67%; ctrl: 66.67%; ctrl: 66.67%; -: 7
| - of which installation [%] | ctrl: 33.33%; ctrl: 33.33%; ctrl: 33.33%; ctrl: 33.33%; ctrl: 33.33%; -: 7
| Fixed O&M [€/MJ/s/year] | 3986 | 3869 | 3810 | 3751 | 3634 |  |  |  |  | C | [2, 1]
| Variable O&M [€/MWh] | 0.167 | 0.167 | 0.167 | 0.167 | 0.167 |  |  |  |  | C | [2, 7]
Technology-specific data
Indirect investments cost [M€/MW] | bar: ctrl to ctrl; -
Notes:
A | The efficiency of the burner is set equal to the lower heating value, the process will determine how well the flue gas is utilised, and thus the final efficiency.
B | Auxilliary consumption based on gas burner as the fan power is comparable. Electricity for fuel feed systems are not included.
C | Assumed to be equal to 10% of the coal boiler O&M from [1]. With gaseous or liquid fuels the O&M will be lower.
D | Depends on the solid fuel mix used
E | Unit price from FLSmidth, installed price and auxilliary equipment assessed by Viegand Maagøe. The assessment is an experience based guess as no concrete data was retrieved.
F | The burner itself can start up quickly. However, in e.g. Cement industry the process equipment will limit the startup time to between 8 (warm) and 72 (cold) hours.
G | Capacity increase in multifuel burners comes with an attractive economy of scale. Going up 10 times in size will correspond toa 150% increase in pricing .
H | Auxilliary systems for solid fuels has been included, these correspond to a large part of the investment and will be a function of the chosen fuel.
I | Corresponds to a burner change, establishing a feed system has a longer construction period.
J | The indirect costs will be too strong a function of the process to put into a single value across all industries.
References:
1 | Danish Energy Agency, Technology Data Generation of Electricity and District Heating, August 2016 - Updated November 2019
2 | Viegand Maagøe, Direct Firing, 2018
3 | Danish Energy Agency, Forudsætninger for samfundsøkonomiske analyser på energiområdet, 2016
4 | FLSmidth - Burner & PLM for HOTDISC, Correspondance 2019
5 | IOGP, The potential for CCS and CCU in Europe, REPORT TO THE THIRTY SECOND MEETING OF THE EUROPEAN GAS REGULATORY FORUM 5-6 JUNE 2019
6 | FCT International Burners, Correspondance 2019.
7 | Viegand Maagøe assessment, 2019
8 | Eclipse, Eclipse AirHeat Burners Datasheet 115-11, 30/9/2010
9 | Eclipse, Eclipse RatioAir Burners Datasheet 135, 21/10/2010

## 7.3 Direct electric firing
Technology |  | Direct electric heating
year |  | 2025 | 2030 | 2035 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | - | -
cat | par
Energy/technical data
| Heat generation capacity for one unit [MW] | 5 | 5 | 5 | 5 | 5 | 1 | 10 | 1 | 10 |  | [1, 2]
| Total efficiency, net [%], nominel load | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | A | [3, 4]
| Total efficiency, net [%], annual average | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | A | [3, 4]
| Auxiliary electricity consumption [% of heat gen] | 0.25% | 0.25% | 0.25% | 0.25% | 0.25% | 0.1% | 1% | 0.1% | 1% | B | [6, 7]
| Forced outage [days] | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0.5 | C | 1
| Planned outage [weeks per year] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | C | 1
| Technical lifetime [years] | ctrl: 20; ctrl: 20; ctrl: 20; ctrl: 20; ctrl: 20; -: 8
| Construction time [years] | ctrl: 0.04; ctrl: 0.04; ctrl: 0.04; ctrl: 0.04; ctrl: 0.04; -: 1
| Space requirement [1000 m2/MW_e] | ctrl: 0.0125; ctrl: 0.005; ctrl: 0.001; ctrl: 0.001; ctrl: 0.001; -: 5
Regulation ability
| Primary regulation (of full load, per 30 seconds) [%] | 100% | 100% | 100% | 100% | 100% |  |  |  |  | G | 11
| Secondary regulation (of full load, per minute) [%] | 100% | 100% | 100% | 100% | 100% |  |  |  |  | G | 11
| Minimum load [% of full load] | 15% | 15% | 15% | 15% | 15% |  |  |  |  | D | 8
| Warm start-up time [hours] | ctrl: 0.01; ctrl: 0.01; ctrl: 0.01; ctrl: 0.01; ctrl: 0.01; -: [5, 9]
| Cold start-up time [hours] | ctrl: 0.01; ctrl: 0.01; ctrl: 0.01; ctrl: 0.01; ctrl: 0.01; -: [5, 9]
Financial data
| Nominal investment (*total) [MEUR/MW] , from last update in 2019 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 |  |  |  |  | E, H | [9, 10]
| - of which equipment [%] | ctrl: 66.67%; ctrl: 66.67%; ctrl: 66.67%; ctrl: 66.67%; ctrl: 66.67%; -: 9
| - of which installation [%] | ctrl: 33.33%; ctrl: 33.33%; ctrl: 33.33%; ctrl: 33.33%; ctrl: 33.33%; -: 9
| Fixed O&M [EUR/MW_y] | 0 | 0 | 0 | 0 | 0 |  |  |  |  | C | 5
| Variable O&M [EUR/MWh] | ctrl: 0.235; ctrl: 0.235; ctrl: 0.235; ctrl: 0.235; ctrl: 0.235; -: C
Technology-specific data
Indirect investments cost [M€ per MW] | bar: ctrl to ctrl; -
Non energy gains [M€ per MW] | bar: ctrl to ctrl; -
Startup cost [€/MW/startup] | bar: ctrl to ctrl; -
| Temperature heat supply, maximum [°C] | ctrl: 1800; ctrl: 2000; ctrl: 2000; ctrl: 2000; ctrl: 2000; -: [4, 5]
Notes:
A | Transformer electricity losses are not included, and the efficiency will thus be 100%.
B | Auxilliary consumption estimation based on conventional industrial systems like gas burner/boilers as the fan power is comparable.
C | Units are composed of multiple heating elements, each unit is installed with backup elements that can be enabled if some of the elements fail, resulting in minimal downtime and O&M during the lifetime of the equipment.
D | The regulation is dependant on the flow conditions and the subsequent surface temperature, the chosen value is an average.
E | Unit price from San Electro Heat, installed price assessed by Viegand Maagøe. The assessment is an experience based guess as no concrete data was retrieved.
F | The indirect costs will be too strong a function of the process to put into a single value across all industries. This includes site updgrades to facilitate the installation of direct firing systems.
G | The electric heating element is able to adjust capacity almost instantly. The surrounding process equipment will be the limiting factor.
H | The cost has been corrected for inflation.
References:
1 | SAN Electro Heat A/S , Correspondance 2019
2 | DTU, "Electrification of processes and technologies for Danish Industry: Elforsk project 350-038", 2021
3 | Viegand Maagøe, Direct Firing, 2018
4 | Renewable Thermal Collaborative, "Electrification Action Plan", 2024
5 | Fraunhofer ISI, "Direct electrification of industrial process heat. An assessment of technologies, potentials and future prospects for the EU. Study on behalf of Agora Industry", 2024
6 | Eclipse, Eclipse AirHeat Burners Datasheet 115-11, 30/9/2010
7 | Eclipse, Eclipse RatioAir Burners Datasheet 135, 21/10/2010
8 | Ashabi et al., "Assessing power-to-heat technologies for industrial electrification: A multi-criteria decision analysis approach", 2025
9 | TNO, Technology factsheet Electric Industrial Boiler, 2018
10 | Viegand Maagøe assessment, 2019
11 | Energy Efficiency and Conservation Authority - New Zealand government, "Electrode and ElectricResistance Steam Generatorsand Hot Water Heaters for low carbon process heating", 2019